## Introduction
Armor PowerFlex CIP Object Definitions
About This Publication | This publication lists the CIP object definitions and attribute values for Armor™ PowerFlex® variable frequency drives.
For more information see:
Armor PowerFlex AC Drives User Manual, publication 35-UM001.
Important: Rockwell Automation is not responsible for any content or format changes made by other parties after downloading this spreadsheet file. The original file can be re-downloaded at any time.
TIP: When you search for information in a spreadsheet, set the search options to search the workbook, rather than the current sheet (tab).
Your comments help us serve your documentation needs better. If you have any suggestions on how to improve our content, complete the form at: |  | rok.auto/docfeedback
Allen-Bradley, Armor, expanding human possibility, PowerFlex, and Rockwell Automation are trademarks of Rockwell Automation, Inc. EtherNet/IP and CIP are trademarks of ODVA, Inc. Trademarks not belonging to Rockwell Automation are property of their respective companies.

## Objects
Armor PowerFlex CIP Object Definitions
For more information see:
Armor PowerFlex AC Drives User Manual, publication 35-UM001.
Class | Object Name | Proposed Description | Group
0x0427 (1063) | Physical Brake Control Supervisor | This object controls the state of an attached or embedded physical brake. It provides generic control operations suitable for various types of brakes, including holding brakes and stopping brakes. The Physical Brake Control Supervisor object takes the data from multiple Physical Brake Control Source instances and decides on a single commanded physical brake state. A physical brake is a device that when engaged prevents motion of a system. If your drive does not include a physical brake, this object is not used. | Braking
0x0428 (1064) | Physical Brake Control Source | This object represents one of many sources of commanded physical brake state and provides data used by the Physical Brake Control Supervisor object (0x0427) to determine the state of the physical brake. If your drive does not include a physical brake, this object is not used. | Braking
0x042B (1067) | Dynamic Brake | This object represents a dynamic brake feature in a motor control device. A dynamic brake feature lets excess power be dumped to a resistor, either internal to the product or external. This feature is typically activated during braking or deceleration, allowing the action to occur more rapidly. | Braking
0x0001 (1) | Identity | This object models a physical device (entire product) or physical subcomponent of a device. | Communications
0x0004 (4) | Assembly | This object defines how input or output data from multiple objects is sent or received over a single connection. An input produces data on the network and an output consumes data from the network. | Communications
0x0006 (6) | Connection Manager | The Connection Manager Class allocates and manages the internal resources associated with both I/O and Explicit Messaging Connections. The specific instance generated by the Connection Manager Class is referred to as a Connection Instance or a Connection Object. | Communications
0x0047 (71) | Device Level Ring | This object provides the configuration and status information interface for the device's DLR protocol implementation. | Communications
0x00F5 (245) | TCP IP Interface | This object provides the mechanism to configure a device's TCP/IP network interface. | Communications
0x00F6 (246) | Ethernet Link | This object maintains counters and status information for an ethernet interface. Every ethernet port on the device has an instance of this object. | Communications
0x0430 (1072) | Fault Auto Clear Run | The fault auto reset and run (auto restart) feature lets certain faults be cleared and the product be commanded back into the running state. See the product user manual for information on which faults are handled by this feature. | Extended Control Configuration
0x0431 (1073) | Flying Start | This object lets you configure the flying start feature and provides status information related to the feature. The flying start feature lets you start a motor that is already in motion. When flying start is enabled, the drive responds to a start command by synchronizing with the motors speed (frequency and phase) and voltage and then accelerating to the desired frequency. This process prevents an overcurrent trip and significantly reduces the time for the motor to reach its desired frequency. | Extended Control Configuration
0x0433 (1075) | Velocity Skip Band | This object lets you configure a band of velocity in which a motor will not run constantly (the commanded velocity is forced outside the band). The logic related to determining if a commanded velocity is in a velocity skip band is often performed in the Velocity Control Supervisor object (0x041E). | Extended Control Configuration
0x0434 (1076) | Load Monitor | This object monitors the drive for conditions where more or less power than expected is being provided to or provided by the motor to drive a particular load. Two types of monitoring can be performed: shear pin and load loss. Shear pin monitors for power greater than the configured level, which may indicate a stuck load. This feature can cause a fault and stop the motor to prevent damage to the motor or load device. Load loss monitors for power less than the configured level, which may indicate that the load is no longer connected to the motor. This feature can stop the motor or trigger an alarm. You can configure the power level, either as an absolute amount of output current being supplied to the motor or a torque value. You can also configure a monitor time, which delays the reporting of a load monitoring condition when the power is above or below the level. | Extended Control Configuration
0x0435 (1077) | Slip Droop Compensation | This object adjusts the output frequency to a motor to take motor slip or droop into account, so that the actual motor velocity more closely matches the commanded velocity. It results in a more consistent velocity independent of the load. When the velocity control is running closed loop (with a feedback device), the amount of motor slip droop is directly measured. When the velocity control is running open loop (without a feedback device), the amount of motor slip/droop is estimated based on the load. When estimating the amount of slip or droop, a default amount of slip or droop compensation at full load is used. This default can be fixed, based on motor type, calculated based on motor configuration data or entered by a user to match actual motor performance more closely. | Extended Control Configuration
0x0417 (1047) | Fault Alarm | This object represents the current state of faults and alarms in a product, and provides an interface for users to acknowledge or clear faults. | Faults, Alarms, and Events
0x042F (1071) | Feedback | This object represents a feedback device (encoder) in a motor or motion control system and serves as an interface to motion sensor devices such as rotary or linear encoders through both analog and digital hardware interfaces. It provides the ability to configure the properties of the feedback device if they cannot be automatically determined and reports the status of the feedback device. | Feedback
0x0424 (1060) | DC Bus | This object represents a DC electrical bus in a product. It can perform voltage level monitoring and reporting. | Inverter
0x0425 (1061) | Inverter | This object represents an inverter that converts a DC electrical power input to an AC output. | Inverter
0x0436 (1078) | Inverter Protection | This object lets you configure a variable frequency drive inverter's overcurrent, overload, and current limit protection features and provides status information related to those features. | Inverter
0x0437 (1079) | Inverter Current Limit Source | This object represents one of many sources of a user defined inverter current limit that can be used by the Inverter Protection object (0x0436). | Inverter
0x041D (1053) | Motor Configuration | This object lets the nameplate or rating data and tuning data for a motor attached to a motion control device be configured. | Motor
0x0422 (1058) | Motor Tuning Data Source | This object represents one of many sources of motor tuning data which can be used by the Motor Configuration object (0x041D) to provide a complete set of tuning data. | Motor
0x0432 (1074) | Motor Thermal Overload | This object lets you configure the motor thermal overload protection feature and provides status information related to the feature. Motor thermal overload protection helps to prevent overheating and possible damage to the connected motor. When the drive detects that the motor is too hot, a thermal overload condition is declared. Power to the motor is removed to allow the motor to cool and the overload condition to clear. When the overload condition is cleared, the motor can be restarted. The protection feature lets the motor to operate at a power level above its overload rating for short periods of time while starting or accelerating to prevent faults from occurring. | Motor
0x0447 (1095) | Control Model Adjustment | This object lets you manually adjust the operating parameters of a motor control model to change the behavior of the model so that you can achieve better control by removing oscillations or instabilities that occur during operation. | Motor
0x041B (1051) | Motor Control Supervisor | This object is controls all motor-related operations in a device. It controls the basic state of the connected motor (stopped or running) and the direction of motion of the motor. | Motor Control
0x041C (1052) | Motor Control Source | This object represents one of many sources of motor control commands. It takes the data from multiple Motor Control Sources and decides which commands are passed to the motion control logic. | Motor Control
0x041E (1054) | Velocity Control Supervisor | This object manages velocity motor control (speed regulation) operations in a device, using data from multiple Velocity Control Source object (0x041F) instances and determining a single commanded velocity to pass through to the motor control (speed regulator). | Motor Control
0x041F (1055) | Velocity Control Source | This object represents one of many sources of commanded velocity. It takes data from multiple Velocity Control Sources and determines a single commanded velocity to pass through to the motor control (speed regulator). | Motor Control
0x0420 (1056) | Acceleration Control Supervisor | This object controls the acceleration and deceleration (ramp) motor control operations in the device. All acceleration and deceleration values in this object are expressed in terms of seconds to go from zero speed to the full rated speed of the attached motor. | Motor Control
0x0421 (1057) | Acceleration Control Source | This object represents one of many sources of commanded acceleration whose data can be used by the Acceleration Control Supervisor object (0x0420) to determine a single set of commanded acceleration parametrs to pass through to the motor control (ramp). | Motor Control
0x0429 (1065) | Stop Control Supervisor | This object controls the motor stop operations in the device, which determine what happens when a stop command is issued. | Motor Control
0x042A (1066) | Stop Control Source | This object represents one of many sources of stop mode and stop settings control, whose data can be used by the Stop Control Supervisor object (0x0429) to determine a single stop mode and other stop settings to pass through to the motor control. | Motor Control
0x042C (1068) | Motor Control Configuration | This object lets you select the motor control mode and motor control method. The motor control mode specifies what motor behavior is being controlled by the device. The motor control method specifies "how" the motor control is being performed. Other objects, specified by an attribute in this object, provide additional configuration for specific motor control methods. | Motor Control
0x042D (1069) | Motor Control Method Frequency | This object lets you configure frequency-based control methods, when the Motor Control Method attribute in the Motor Control Configuration object (0x042C) is set to Frequency. | Motor Control
0x042E (1070) | Motor Control Method Vector | This object lets you configure vector-based control methods, when the Motor Control Method attribute in the Motor Control Configuration object (0x042C) is set to Vector. | Motor Control
0x043D (1085) | Velocity Preset | This object represents the configurable motor control velocity (speed reference) presets in a device. | Motor Control
0x043E (1086) | Acceleration Preset | This object represents the configurable motor control acceleration or deceleration time and S-curve settings in a device. | Motor Control
0x043F (1087) | Discrete Output Control Source | This object represents one of many sources of control of an individual discrete output point. In products with multiple sources of control for one physical discrete output, the Discrete Output Point object takes the data from multiple Discrete Output Control Source instances and determines the proper state of the output. | Motor Control
0x0446 (1094) | Jog Preset | This object represents the configurable jog motor control preset values in a device, including a velocity used to set motor speed while the motor is jogging. It can also include information about acceleration and direction. | Motor Control
0x0423 (1059) | Temperature Sensor | This object represents a product's temperature sensor device and provides the ability to monitor temperature. | Physical
0x0426 (1062) | Power Supply | This object represents either an internal or external electrical power supply and can report data such as measured output voltage and the load on the power supply. It can perform monitoring of the voltage level of the power supply or output current and report events when those values are outside of the specified limits. | Physical
0x0438 (1080) | Drive Power Loss Supervisor | This object monitors one or more active power loss sources and takes action when a power loss condition occurs in a drive device. If a power loss is detected, the configured power loss immediate action is triggered. | Physical
0x0439 (1081) | Drive Power Loss Source | This object represents one of many sources of power loss condition detection and lets you specify an how the power loss is detected and what action to take if a power loss condition is present. | Physical
0x0440 | Fan | This object represents either an internal or external electric fan and can monitor fan speed, reporting events when the speed is outside of specified limits. | Physical
0x0414 (1044) | Predictive Maintenance Component | This object provides a way to indicate predictive maintenance data and status for an individual physical component in a product so that it can be communicated via the user interface. Additionally, this object allows predictive maintenance data to be reset after service to or replacement of a component. Multiple instances of this object represent the various physical components with predictive maintenance information in a product. | Predictive Maintenance
0x0415 (1045) | Predictive Maintenance Component Group | This object organizes and categorizes the Predictive Maintenance Component objects and helps make it easier to discover and collect predictive maintenance data for specific component types. Additionally, this object allows event thresholds and event actions to be configured for all components within the group. Multiple instances of this object represent the various collections of components in a product. | Predictive Maintenance
0x0039 (57) | Safety Supervisor | This object defines the behavior model of safety devices. | Safety
0x003B (59) | Safety Discrete Output Point | This object models the discrete safety outputs of a product. An output consumes data from the network. | Safety
0x003D (61) | Safety Discrete Input Point | This object models the discrete safety inputs of a product. An input produces data from the network. | Safety
0x0058 (88) | Safety Feedback | This object provides an interface to motion sensor devices like rotary or linear encoders. | Safety
0x005A (90) | Safety Stop Functions | This object provides an interface to designated safety functions like safe torque off, safe stop 1, and safe brake control. | Safety
0x0348 (840) | Safety Dual Channel Input | This object models a pair of safety input channels as Safety Dual Channel Inputs in a product. An input produces data from the network. | Safety
0x008 (8) | Discrete Input Point | This object models the discrete outputs of a product. An output consumes data from the network. | Standard I/O
0x009 (9) | Discrete Output Point | This object models the discrete inputs of a product. An input produces data from the network. | Standard I/O

## Data Types
Armor PowerFlex CIP Object Definitions
For more information see:
Armor PowerFlex AC Drives User Manual, publication 35-UM001.
These data types are referenced in this publication.
Type | Definition | Range
BOOL | Boolean - defined by the CIP standard to be an 8-bit unsigned integer with enumeration of 0 for False and 1 for True. | 0, 1
BYTE | Bit string - 8 bits | —
DINT | Double integer | -231 DINT (231 – 1)
EPATH | A logically encoded series of path segments to provide the address of a “value” or “data” within a CIP Object. Also called an Internal Object Identifier (IOI) | —
INT | Integer | -32768 INT 32767
LINT | Long integer | -263 LINT (263 – 1)
REAL | Single precision float. | See IEEE 754.
SHORT STRING | {length, 1-byte characters[n]} | —
SINT | Short integer | -128 SINT 127
UDINT | Unsigned double integer | 0 UDINT (232 – 1)
UINT | Unsigned integer | 0 UINT 65536
ULINT | Unsigned long integer | 0 ULINT (264 – 1)
USINT | Unsigned short integer | 0 USINT 255
WORD | Bit string - 16 bits | —

## Braking Objects
Armor PowerFlex CIP Object Definitions
For more information see:
Armor PowerFlex AC Drives User Manual, publication 35-UM001.
Class | Name | Instance | Attribute | Attribute Name | Data Classification | Access Rule | Data Type | Description | Attribute Values
0x0427 (1063) | Physical Brake Control Supervisor | 1=EM Brake | 1 | Active Source | Status | Get | UINT | Instance number of Physical Brake Control Source (0x0428)instance currently actively controlling motor operation in the device. | 0=No active control source. Brake is in the engaged state. 1=Automatic 2=Manual assembly 3=Manual assembly class 3
0x0427 (1063) | Physical Brake Control Supervisor | 1=EM Brake | 100 | State Commanded | Status | Get | BOOL | Indicates what state the brake is being commanded to be in. | 0=Brake is commanded to be in the engaged state. 1=Brake is commanded to be in the released state.
0x0427 (1063) | Physical Brake Control Supervisor | 1=EM Brake | 101 | State Actual | Status | Get | BOOL | Indicates the actual state of the physical brake or physical brake output. | 0=Brake is engaged 1=Brake is released.
0x0427 (1063) | Physical Brake Control Supervisor | 1=EM Brake | 102 | State Discrepancy Check Enable | Configuration | Set(1) | BOOL | Enables the drive to detect a discrepancy between the commanded and actual states. | 0=Disable discrepancy checking. (default) 1=Enable discrepancy checking.
0x0427 (1063) | Physical Brake Control Supervisor | 1=EM Brake | 103 | Allowed State Discrepancy Time | Configuration | Set(1) | REAL | If the state discrepancy check is enabled, this attribute defines the maximum amount of time a discrepancy can exist before the State Discrepancy Present attribute (104) is set to true. | 0…10.0 seconds (default =2)
0x0427 (1063) | Physical Brake Control Supervisor | 1=EM Brake | 104 | State Discrepancy Present | Status | Get | BOOL | When discrepancy checking is active, this value indicates whether a discrepancy between the State Commanded and State Actual attributes has been detected for longer than the Allowed State Discrepancy Time (attribute 103). It is automatically cleared when the discrepancy no longer exists. | 0=State discrepancy is no longer detected 1=A state discrepancy has persisted for longer than the Allowed State Discrepancy Time (attribute 103).
0x0427 (1063) | Physical Brake Control Supervisor | 1=EM Brake | 105 | Release Time | Configuration | Set(1) | REAL | Time it takes for the brake to release after it is commanded to do so. This time may be used in algorithms that automatically control the brake. | 0…10.0 seconds (default =2)
0x0427 (1063) | Physical Brake Control Supervisor | 1=EM Brake | 106 | Engage Time | Configuration | Set(1) | REAL | Time it takes for the brake to engage after it is commanded to do so. This time may be used in algorithms that automatically control the brake. | 0…10.0 seconds (default =2)
0x0427 (1063) | Physical Brake Control Supervisor | 1=EM Brake | 109 | Fuse State | Status | Get | BOOL | Indicates the state of a fuse or circuit breaker protecting a brake control circuit. | 0=The fuse or circuit breaker is in the closed state. 1=The fuse or circuit breaker is in the open state.
0x0428 (1064) | Physical Brake Control Source | 1=Automatic 2=Manual Assembly 3=Manual Assembly Class 3 | 1 | Enable | Configuration | Set(1) | BOOL | Lets the source be enabled or disabled. When enabled, the source can become operational. | 0=Source disabled (default for instances 1 and 3) 1=Source enabled (default for instance 2)
0x0428 (1064) | Physical Brake Control Source | 1=Automatic 2=Manual Assembly 3=Manual Assembly Class 3 | 2 | Inhibit | Control | Set | BOOL | Lets the source be inhibited and temporarily disabled (ignored). While inhibited, it cannot become the active control source. | 0=Source is not inhibited and can become the active source. (default) 1=Source is inhibited.
0x0428 (1064) | Physical Brake Control Source | 1=Automatic 2=Manual Assembly 3=Manual Assembly Class 3 | 3 | Operational | Status | Get | BOOL | Indicates whether the source instance is currently operational. | 0=Source is not operating and cannot become the active source. 1=Source is operating and can become the active source.
0x0428 (1064) | Physical Brake Control Source | 1=Automatic 2=Manual Assembly 3=Manual Assembly Class 3 | 4 | Operational State | Status | Get | USINT | Indicates the operational state or operating condition of the source. | 0=OK: Source is operating normally. 1=Data Invalid: Source is operating, but one or more input data attributes are invalid and should not be used. 2=Faulted: Source has experienced a fault condition while operating. Logic related to the source may not be running or may be only partially active.
0x0428 (1064) | Physical Brake Control Source | 1=Automatic 2=Manual Assembly 3=Manual Assembly Class 3 | 5 | Priority | Constant | Get | UINT | Indicates the order in which multiple operational sources are considered when a single active source needs to be determined. Higher values mean greater priority in the active source determination. If two values share the same priority value, priority is determined by instance number (lowest instance number has highest priority). | Instance 1=70 Instance 2=90 Instance 3=80
0x0428 (1064) | Physical Brake Control Source | 2=Manual Assembly | 9 | Action Data Invalid | Configuration | Set(1) | USINT | Defines the action that the source should perform when the operational state changes from OK to Data Invalid. Lets you configure a proper response to conditions where no valid data is available. | 0=None: No action is taken; the source remains operational. 1=Invalidate: Source is invalidated and is no longer operational. Lower priority sources can become active. (default?) 2=Fault: A Data Invalid, Fault is declared. Source is invalidated. 3=Alarm: A Data Invalid, Alarm is declared. Source is invalidated. 4=Safe State: The data for the source is placed in a safe state; source remains operational.
0x0428 (1064) | Physical Brake Control Source | 2=Manual Assembly 3=Manual Assembly Class 3 | 10 | Action Faulted | Configuration | Set(1) | USINT | Defines the action that the source should perform when the operational state changes from OK to Faulted. Lets you configure a proper response to conditions where the source is faulted. | 0=None: No action is taken; the source remains operational. 1=Invalidate: Source is invalidated and is no longer operational. Lower priority sources can become active. 2=Fault: A Source Faulted, Fault is declared. Source is invalidated. 3=Alarm: A Source Faulted, Alarm is declared. Source is invalidated. 4=Safe State: The data for the source is placed in a safe state; source remains operational.
0x0428 (1064) | Physical Brake Control Source | 1=Automatic 2=Manual Assembly 3=Manual Assembly Class 3 | 12 | Valid | Status | Get | BOOL | Indicates whether the source should be used as the active control source even if it is enabled and not inhibited. | 0=Source should not be used as the active control source even if it is enabled and not inhibited. 1=Source is valid and should be used.
0x0428 (1064) | Physical Brake Control Source | 2=Manual Assembly 3=Manual Assembly Class 3 | 100 | State | Control | Set | BOOL | Defines the physical brake state to be commanded by the Physical Brake Control Supervisor object (0x0427). | 0=Brake is commanded to be in the engaged state. (default) 1=Brake is commanded to be in the released state.
0x042B (1067) | Dynamic Brake | 1=Dynamic Brake | 1 | Active | Status | Get | BOOL | Indicates whether the dynamic brake is active. | 0=Dynamic brake is not active 1=Dynamic brake is active.
0x042B (1067) | Dynamic Brake | 1=Dynamic Brake | 2 | Resistor Overtemperature | Status | Get | BOOL | Indicates whether the dynamic brake resistor is over its designed maximum temperature. When this attribute is true (1), the dynamic brake feature is automatically disabled to protect the hardware. | 0=Dynamic brake resistor is operating within its designed temperatures limits. 1=Dynamic brake resistor is operating above its designed temperature limit.
0x042B (1067) | Dynamic Brake | 1=Dynamic Brake | 100 | Enabled | Configuration | Set(1) | BOOL | Selects whether the dynamic brake feature is enabled or disabled. | 0=Disabled (default) 1=Enabled
0x042B (1067) | Dynamic Brake | 1=Dynamic Brake | 101 | Threshold | Configuration | Set(1) | REAL | Defines the DC bus voltage at which the dynamic brake can be activated. | 77.0…850.0 Volts (default=770.0)
0x042B (1067) | Dynamic Brake | 1=Dynamic Brake | 102 | Resistor Type | Configuration | Set(1) | UINT | Selects the type of resistor being used for the dynamic brake feature. | 0=Not Specified (default) 3=External Light Duty: Resistor parameters are fixed at product specific values. 4=External Normal Duty: Resistor parameters are fixed at product specific values.
-1 | Configuration attributes are settable through the user interface of the configuration software. If changes are made by using another method, the changed values may be overwritten when a connection is re-established or the device is power cycled.

## Communication Objects
Armor PowerFlex CIP Object Definitions
For more information see:
Armor PowerFlex AC Drives User Manual, publication 35-UM001.
Class | Name | Instance | Attribute | Attribute Name | Data Classification | Access Rule | Data Type | Description | Attribute Values
0x0001 | Identity | 1=Product | 1 | Vendor Id | Constant | Get | UINT | Identifies each vendor by number. | 1=Rockwell Automation
0x0001 (1) | Identity | 1=Product | 2 | Device Type | Constant | Get | UINT | Identifies the general type of product. | 170=PowerFlex Device
0x0001 (1) | Identity | 1=Product | 3 | Product Code | Constant | Get | UINT | Identifies the specific product. | 0x0002=Bulletin 35S Armor PowerFlex Drives 0x0003=Bulletin 35E Armor PowerFlex Drives
0x0001 (1) | Identity | 1=Product | 4 | Revision | Constant | Get | UINT | The revision of the instance item that the Identity Object represents. This is the firmware revision of the product. | —
0x0001 (1) | Identity | 1=Product | 5 | Status | Status | Get | UINT | A summary of device status. | Bit ¦ Value (0=False, 1=True) Bit 2=Configured Bits 4…7=Extended Status • 1=Firmware update • 2=At least one faulted I/O connection • 3=no I/O connections established • 4=Non-volatile configuration bad • 5=Major fault • 6=At least one I/O connection is in Run mode • 7=At least one I/O connection is established, all in Idle mode • 8=Not applicable • 9=Reserved Bit 10=Major recoverable fault
0x0001 (1) | Identity | 1=Product | 6 | Serial Number | Constant | Get | UDINT | The serial number of the device. | —
0x0001 (1) | Identity | 1=Product | 7 | Product Name | Constant | Get | STRING | The product name. | —
0x0001 (1) | Identity | 1=Product | 19 | Protection Mode | Status | Get | UINT | The current protection mode of the device. | 0=Implicit Protection Enabled 3=Explicit Protection Enabled
0x0001 (1) | Identity | 1=Product | 20 | Uptime | Status | Get | UDINT | The amount of time, in seconds, since the device was last powered up or restarted. | —
0x0001 (1) | Identity | 1=Product | 21 | Catalog Number | Constant | Get | STRING | The product catalog number. | —
0x0001 (1) | Identity | 1=Product | 22 | Manufacture Date | Constant | Get | UINT | The date the product was manufactured. | —
0x0001 (1) | Identity | 1=Product | 35 | Warranty Number | Constant | Get | STRING | The value used for tracking warranty. | —
0x0001 (1) | Identity | 1=Product | 37 | Hardware Revision | Constant | Get | UINT | The revision of the hardware for the item the Identity Object represents. | —
0x0001 (1) | Identity | 1=Product | 101 | Hardware Revision | Constant | Get | UINT | The revision of the hardware for the item the Identity Object represents. | —
0x0001 (1) | Identity | 1=Product | 102 | Subminor | Constant | Get | UDINT | The subminor (last) position of the Firmware revision number. | —
0x0001 (1) | Identity | 1=Product | 113 | Warranty Number | Constant | Get | STRING | The value used for tracking warranty. | —
0x0001 (1) | Identity | 1=Product | 114 | Series | Constant | Get | STRING | The product series. | —
0x0004 (4) | Assembly | 1025=InputVFD 13313=InputVFDClass3 769=OutputVFD 13057=OutputVFDClass3 | 3 | Data | Control | Set | Array of BYTES | Identifies assembly data as an array of bytes. | See the I/O and Drive Assemblies Appendix in the user manual.
0x0004 (4) | Assembly | 1025=InputVFD 13313=InputVFDClass3 769=OutputVFD 13057=OutputVFDClass3 | 4 | Size | Status | Get | UINT | The number of bytes of data present in the Data attribute. | See the I/O and Drive Assemblies Appendix in the user manual.
0x0006 (6) | Connection Manager | 1=Manager | 1 | Open Requests | Status | Get | UINT | The number of Forward Open service requests received. | —
0x0006 (6) | Connection Manager | 1=Manager | 2 | Open Format Requests | Status | Get | UINT | The number of Forward Open service requests rejected due to bad format. | —
0x0006 (6) | Connection Manager | 1=Manager | 3 | Open Resource Rejects | Status | Get | UINT | The number of Forward Open service requests rejected due to lack of resources. | —
0x0006 (6) | Connection Manager | 1=Manager | 4 | Open Other Rejects | Status | Get | UINT | The number of Forward Open service requests rejected due to reasons other than bad format or lack or resources. | —
0x0006 (6) | Connection Manager | 1=Manager | 5 | Close Requests | Status | Get | UINT | The number of Forward Close service requests received. | —
0x0006 (6) | Connection Manager | 1=Manager | 6 | Close Format Rejects | Status | Get | UINT | The number of Forward Close service requests rejected due to bad format. | —
0x0006 (6) | Connection Manager | 1=Manager | 7 | Close Other Rejects | Status | Get | UINT | The number of Forward Close service requests rejected for reasons other than bad format. | —
0x0006 (6) | Connection Manager | 1=Manager | 8 | Connection Timeouts | Status | Get | UINT | The total number of connection timeouts that have occurred in connections controlled by this Connection Manager. | —
0x0006 (6) | Connection Manager | 1=Manager | 11 | CPU Utilization | Status | Get | UINT | CPU utilization in tenths of a percent. | —
0x0006 (6) | Connection Manager | 1=Manager | 15 | I/O Packets per Second | Status | Get | UINT | The Current I/O packets per second for I/O traffic. | —
0x0006 (6) | Connection Manager | 1=Manager | 16 | Percent I/O Utilization | Status | Get | UINT | The current I/O communications utilization for I/O traffic. | —
0x0006 (6) | Connection Manager | 1=Manager | 17 | Explicit Packets Per Second | Status | Get | UINT | Total number of explicit packets sent and received by this device over the last second. | —
0x0006 (6) | Connection Manager | 1=Manager | 18 | Missed I/O Packets | Status | Get | UINT | A running total of missed I/O packets. | —
0x0006 (6) | Connection Manager | 1=Manager | 19 | CIP I/O Connections | Status | Get | UDINT | The total number of CIP I/O connections in use. | —
0x0006 (6) | Connection Manager | 1=Manager | 20 | CIP Explicit Connections | Status | Get | UDINT | Total number of CIP Explicit Messaging connections in use. | —
0x0047 (71) | Device Level Ring | 1=Device Level Ring | 1 | Network Topology | Status | Get | USINT | Indicates the current network topology mode. | 0 = Linear, 1 = Ring
0x0047 (71) | Device Level Ring | 1=Device Level Ring | 2 | Network Status | Status | Get | USINT | Indicates the current status of network. | 0 = Normal 1 = Ring Fault 2 = Unexpected Loop Detect 3 = Partial Network Fault 4 = Rapid Fault/Restore Cycle
0x0047 (71) | Device Level Ring | 1=Device Level Ring | 10 | Active Supervisor Address | Status | Get | STRING | Indicates the IP and/or MAC address of the active ring supervisor. | 0=No address configured yet other values are device-specific
0x0047 (71) | Device Level Ring | 1=Device Level Ring | 12 | Capability Flags | Status | Get | UDINT | Describes the DLR capabilities of the device. | Bit 1=Beacon-based Bit 7=Flush table frame capable
0x00F5 (245) | TCP IP Interface | 1=TCP IP Interface | 1 | Status | Status | Get | UDINT | Indicates the status of the interface | 0=Not configured 1=Valid configuration
0x00F5 (245) | TCP IP Interface | 1=TCP IP Interface | 2 | Configuration Capability | Status | Get | UDINT | Identifies the capabilities of the interface. | Bit ¦ Value (0=False, 1=True) 0=Supports BOOTP 1=DNS Client (able to resolve host names by query to DNS server) 2=DHCP Client (able to obtain network configuration through DHCP) 3=DHCP-DNS Update (able to send its host name in the DHCP request) 4=Configuration Settable (able to set the network configuration via TCP/IP object)
0x00F5 (245) | TCP IP Interface | 1=TCP IP Interface | 3 | Configuration Control | Configuration | Set(1) | UDINT | Identifies the startup configuration method when network switches are set to 999. | 0=Static IP (Use configuration that is saved in NVS) 1=Obtain configuration via BOOTP 2=Obtain configuration via DHCP (default)
0x00F5 (245) | TCP IP Interface | 1=TCP IP Interface | 4 | Physical Link Object | Status | Get | STRING | Indicates the path to the physical link object, including the path size. | Device-specific
0x00F5 (245) | TCP IP Interface | 1=TCP IP Interface | 5 | Interface Configuration | Configuration | Set(1) | See Description. | Defines the TCP/IP network interface configuration. Including: • IP Address (UDINT) • Network Mask (UDINT) • Gateway Address (UDINT) • Primary DNS (UDINT) • Secondary DNS (UDINT) • Default Domain Name for not fully qualified host names (STRING) | See Description. 0= Not configured.
0x00F5 (245) | TCP IP Interface | 1=TCP IP Interface | 6 | Host Name | Configuration | Set(1) | STRING | Indicates the host name when using DHCP. | Device-specific 0=No host name configured.
0x00F5 (245) | TCP IP Interface | 1=TCP IP Interface | 7 | Safety Network Number | Status | Get | 6 octets | A unique number that identifies the section of a safety network on which the device resides. | Device-specific
0x00F5 (245) | TCP IP Interface | 1=TCP IP Interface | 10 | Select ACD | Constant | Get | BOOL | Indicates the use of Address Conflict Detection (ACD) | 1=Enable ACD
0x00F5 (245) | TCP IP Interface | 1=TCP IP Interface | 11 | Last Conflict Detected | Status | Get | See Description. | Structure containing information about the last conflict detected. • AcdActivity (USINT): State of ACD activity when the last conflict was detected • RemoteMAC (Array of 6 USINT): MAC Address of the remote node in which the last conflict was detected • ArpPdu (Array of 28 USINT): A copy of the ARP PDU in which the conflict was detected | —
0x00F5 (245) | Encapsulation Inactivity Timeout | 1=TCP IP Interface | 13 | Last Conflict Detected | Configuration | Set(1) | UINT | Number of seconds of inactivity before TCP connection is closed | 0 = Disable timeout 1…3600 = timeout in seconds Default = 120
0x00F5 (245) | TCP IP Interface | 1=TCP IP Interface | 14 | IANA Port Admin | Status | Get | See Description. | Structure containing information about the IANA port administration configuration. • Port Count (USINT): Number of elements • Port Array: - Port Name (SHORT STRING) - Port Number (UINT) - Protocol (USINT): 6=TCP; 17=UDP - Admin State (BOOL): 0=Closed; 1=Open - Admin Capability (BYTE) | —
0x00F5 (245) | TCP IP Interface | 1=TCP IP Interface | 15 | IANA Protocol Admin | Status | Get | See Description. | Structure containing information about the IANA protocol administration configuration. • Protocol Count (USINT) • Protocol Array - Protocol Name (SHORT STRING) - Protocol Number (USINT) - Admin State (BOOL): 0=Disabled; 1=Enabled - Admin Capability (BYTE) | —
0x00F5 (245) | TCP IP Interface | 1=TCP IP Interface | 16 | Active TCP Connections | Status | Get | UNIT | Indicates the number of active TCP conection in use. | —
0x00F5 (245) | TCP IP Interface | 1=TCP IP Interface | 17 | Non-CIP Encapsulation Messages Per Second | Status | Get | UDINT | Provides a count of non-CIP encapsulated messages that were sent or received within the last second. | —
0x00F5 (245) | TCP IP Interface | 1=TCP IP Interface | 100 | Address Switch Setting | Status | Get | USINT | Structure containing the type of switch and switch values: • Switch type (USINT) = 1 = standard address switch • Size of switch value array (USINT) • Switch values (array of USINT) 1 element for each physical address switch, returned in order of most-significant to least-significant. | —
0x00F6 (246) | Ethernet Link | 1=Ethernet Port 1 2=Ethernet Port 2 | 1 | Interface Speed | Status | Get | UDINT | Identifies the interface speed currently in use. | 10, 100, or 1000 Mbps
0x00F6 (246) | Ethernet Link | 1=Ethernet Port 1 2=Ethernet Port 2 | 2 | Interface Flags | Status | Get | UDINT | Provides interface status flags. | Bit0=Link status: 0=Inactive; 1=Active Bit1=Half/full duplex: 0=Half duplex; 1=Full duplex Bits2…4=Negotiation status: 0=Auto-negotiation in progress; 1=Auto-negotiation and speed detection failed; 2=Auto negotiation failed but detected speed; 3 = Successfully negotiated speed and duplex; 4=Auto-negotiation not attempted. Forced speed and duplex. Bit5=Manual setting requires release. Bit6=Local hardware fault:0=No fault;1=Fault detected
0x00F6 (246) | Ethernet Link | 1=Ethernet Port 1 2=Ethernet Port 2 | 3 | Physical Address | Status | Get | STRING | Shows the MAC layer address. | —
0x00F6 (246) | Ethernet Link | 1=Ethernet Port 1 2=Ethernet Port 2 | 4 | Interface Counters | Status | Get | See Description. | Structure (of UDINT) of Counters (packets, bytes, errors) for the interface. • In Octets: octets received • In Ucast packets: Unicast packets received • In NUcast packets: Non-unicast packets received • In Discards: Inbound packets received but discarded • In Errors: Inbound packets with errors • In Unknown Protos: Inbound packets with unknown protocol • Out Octets: Octets sent • Out Ucast packets:Unicast packets sent • Out NUcast packets: Non-unicast packets sent • Out Discards: Outbound packets discarded • Out Errors: Outbound packets with errors | —
0x00F6 (246) | Ethernet Link | 1=Ethernet Port 1 2=Ethernet Port 2 | 5 | Media Counters | Status | Get | STRING | Structure (of UDINT) of counters for media-related errors. • Alignment Errors • FCS Errors • Single Collisions • SQE Test Errors • Deferred Transmits • Late Collisions • Excessive Collisions • MAC Transmit Errors • Carrier Sense Errors • Frame Too Long • MAC Receive Errors | —
0x00F6 (246) | Ethernet Link | 1=Ethernet Port 1 2=Ethernet Port 2 | 6 | Interface Control | Configuration | Set(1) | See Description. | Configuration for physical interface: • Interface control bits (WORD): See Attribute Values. • Forced interface speed in Mbps(UINT): 10 or 1000 Mbps | Control Bits: Bit 0=Auto-negotiate: 0=Disabled; 1=Enabled Bit 1=Forced duplex mode: 0=Half duplex; 1=Full duplex
0x00F6 (246) | Ethernet Link | 1=Ethernet Port 1 2=Ethernet Port 2 | 7 | Interface Type | Status | Get | USINT | Indicates the type of physical interface. | 0=Unknown 1=Internal to device 2=Twisted-pair 3=Optical fiber 4=In-Cabinet EtherNet/IP Usage Profile ribbon cable and 10BASE-T1S
0x00F6 (246) | Ethernet Link | 1=Ethernet Port 1 2=Ethernet Port 2 | 8 | Interface State | Status | Get | USINT | Indicates the current operational state of the interface. | 0=Unknown 1=Enabled and ready to receive data 2=Disabled 3=Testing
0x00F6 (246) | Ethernet Link | 1=Ethernet Port 1 2=Ethernet Port 2 | 9 | Admin State | Configuration | Set(1) | USINT | Defines the administrative setting of the interface state. | 0=Reserved 1=Enable interface 2=Disable interface
0x00F6 (246) | Ethernet Link | 1=Ethernet Port 1 2=Ethernet Port 2 | 10 | Interface Label | Status | Get | STRING | Indicates the type of Interface | —
0x00F6 (246) | Ethernet Link | 1=Ethernet Port 1 2=Ethernet Port 2 | 11 | Interface Capability | Status | Get | STRING | Structure that indicates the capabilities of the interface. • Capability Bits (DWORD). See Attribute Values. • Speed/Duplex Array Count (USINT): number of elements. • Speed Duplex Array - Interface Speed (UINT): 10 or 1000 Mbps - Interface Duplex Mode (USINT): 0=half duplex; 1=full duplex | Capability Bits: Bit0=Manual setting requires reset: 0=No reset required; 1=Reset required Bit1= Auto-negotiate: 0=Link auto-negotiation not supported; 1=Link auto-negotiation supported Bit2=Auto-MDIX: 0=Auto-MDIX not supported; 1=Auto-MDIX supported
0x00F6 (246) | Ethernet Link | 1=Ethernet Port 1 2=Ethernet Port 2 | 12 | HC Interface Counters | Status | Get | ULINT | Structure of ULINT identifying the High Capacity Interface Counters: • HCInOctets: Total number of octets received. • HCInUcastPkts: Unicast packets received. • HCInMulticastPkts: Multicast packets received. • HCInBroadcastPkts: Broadcast packets received. • HCOutOctets: Octets sent. • HCOutUcastPkts: Unicast packets sent. • HCOutMulticastPkts: Multicast packets sent. • HCOutBroadcastPkts: Broadcast packets sent. | —
0x00F6 (246) | Ethernet Link | 1=Ethernet Port 1 2=Ethernet Port 2 | 13 | HC Media Counters | Status | Get | ULINT | Structure of ULINT identifying the High Capacity Media Counters: • HCStatsAlignment Errors: Frames received that are not an integral number of octets in length and do not pass FSC check. • HCStatsFCSErrors: Frames received that are an integral number of octets in length but do not pass FSC check. • HCStatsInternalMacTransmitErrors: Frames where transmission failed due to an internal MAC sublayer transmit error. • HCStatsFrameTooLongs: Frames that exceeded the maximum size. • HCStatsInternalMacReceiveErrors:Frames where reception failed due to and internal MAC sublayer receive error. • HCStatsSymbolErrors:Counts the number of times an invalid data symbol was on the media when a valid carrier was present. | —
0x00F6 (246) | Ethernet Link | 1=Ethernet Port 1 2=Ethernet Port 2 | 14 | Ethernet Errors | Status | Get | UDINT | The sum of the values from the following specific members of the Ethernet Link object instance attributes: • Interface Counters, Attribute 4: In Discards, In Errors, Out Discards, Out Errors • Media Counters, Attribute 5: All members • HC Media Counters, Attribute 13 (if supported): HCStatsSymbolErrors. | —
0x00F6 (246) | Ethernet Link | 1=Ethernet Port 1 2=Ethernet Port 2 | 15 | Link Down Counter | Status | Get | UDINT | Counts the number of times a Link Down transition event was detected on this port. | —
-1 | Configuration attributes are settable through the user interface of the configuration software. If changes are made by using another method, the changed values may be overwritten when a connection is re-established or the device is power cycled.

## Extended Control Objects
Armor PowerFlex CIP Object Definitions
For more information see:
Armor PowerFlex AC Drives User Manual, publication 35-UM001.
Class | Name | Instance | Attribute | Attribute Name | Data Classification | Access Rule | Data Type | Description | Attribute Values
0x0430 (1072) | Fault Auto Clear Run | 1=Auto Restart | 101 | Auto Reset Run Enable | Configuration | Set(1) | BOOL | Enables the fault auto reset and run feature. | 0=Fault auto reset and run is disabled. (default) 1=Fault auto reset and run is enabled.
0x0430 (1072) | Fault Auto Clear Run | 1=Auto Restart | 102 | Auto Reset Run Retries | Configuration | Set(1) | UINT | Defines the maximum number of times the drive attempts to reset a fault and restart. | 1…9 Default=1
0x0430 (1072) | Fault Auto Clear Run | 1=Auto Restart | 103 | Auto Reset Run Delay | Configuration | Set(1) | REAL | Defines the time delay between when a fault occurs and when it is automatically reset and the device is restarted. | 1.0…120.0 seconds Default=1 second
0x0430 (1072) | Fault Auto Clear Run | 1=Auto Restart | 105 | Auto Reset Run Active | Status | Get | BOOL | Indicates whether the fault auto reset and run feature is in the active state. | 0=Fault auto reset and run feature is not in the active state. 1=Fault auto reset and run feature is in the active state.
0x0430 (1072) | Fault Auto Clear Run | 1=Auto Restart | 106 | Auto Reset Run Delaying | Status | Get | BOOL | Indicates whether the fault auto reset and run is active but waiting to clear an unacknowledged fault. | 0=Fault auto reset and run feature is not in the active state. 1=Fault auto reset and run feature is in the active state and waiting to clear an acknowledged fault.
0x0430 (1072) | Fault Auto Clear Run | 1=Auto Restart | 107 | Auto Reset Run Attempts | Status | Get | UINT | Indicates the number of fault reset and run attempts that have been made since a power cycle or last time the auto fault clear feature was inactivated. | —
0x0431 (1073) | Flying Start | 1=Flying Start Configuration | 1 | Enable | Configuration | Set(1) | BOOL | Enables the flying start feature. | 0=Flying start disabled. (default) 1=Flying start enabled.
0x0431 (1073) | Flying Start | 1=Flying Start Configuration | 4 | Current Limit | Configuration | Set(1) | REAL | Defines the maximum current, in percentage of product rated current, that is used during motor speed measurement. | 30.0…200.0% Default=150.0%
0x0431 (1073) | Flying Start | 1=Flying Start Configuration | 100 | Active | Status | Get | BOOL | Indicates whether the flying start feature is currently active. The flying start feature is considered active when a start command has been issued and the device is in a state where it is trying to determine the speed of the connected motor. | 0=Flying start is inactive. 1=Flying start is active.
0x0433 (1075) | Velocity Skip Band | 1=Velocity Skip Band 1 2=Velocity Skip Band 2 3=Velocity Skip Band 3 4=Velocity Skip Band 4 | 1 | Enable | Configuration | Set(1) | BOOL | Enables a velocity skip band instance for use. | 0=Velocity skip band is disabled. (default) 1=Velocity skip band is enabled.
0x0433 (1075) | Velocity Skip Band | 1=Velocity Skip Band 1 2=Velocity Skip Band 2 3=Velocity Skip Band 3 4=Velocity Skip Band 4 | 2 | Center | Configuration | Set(1) | REAL | Defines the center or central velocity of the velocity skip band. | 0…500 revolutions per second Default=0.0 revolutions per second
0x0433 (1075) | Velocity Skip Band | 1=Velocity Skip Band 1 2=Velocity Skip Band 2 3=Velocity Skip Band 3 4=Velocity Skip Band 4 | 3 | Width | Configuration | Set(1) | REAL | Defines the width of the velocity skip band. The width is split, with half of it occuring above the center velocity and the other half occurring below the center velocity. If the commanded velocity is in the lower half of the band, the velocity is forced to the center velocity minus half of the band width. If the commanded velocity is in the upper half of the band, it is forced to the center velocity plus half the band width. | 0…60 revolutions per second Default=0.0 revolutions per second
0x0434 (1076) | Load Monitor | 1=Shear Pin 1 2=Shear Pin 2 3=Load Loss 1 | 1 | Type | Constant | Get | USINT | Indicates the type of load monitoring being performed by the instance, monitoring for power above or below the level. | For Shear Pin 1 and Shear Pin 2 instances (1 and 2)= 0: Monitor Above Level, Shear Pin. The instance is checking for power levels above the configured level, implementing a shear pin feature. For Load Loss instance (3)=1: Monitor Below Level, Load Loss. The instance is checking for power levels below the configured level, implementing a load loss feature.
0x0434 (1076) | Load Monitor | 1=Shear Pin 1 2=Shear Pin 2 3=Load Loss 1 | 2 | Enable | Configuration | Set(1) | BOOL | Enables a load monitoring instance for use. | 0=Instance is not enabled for load monitoring. (default) 1=Instance is enabled for load monitoring.
0x0434 (1076) | Load Monitor | 1=Shear Pin 1 2=Shear Pin 2 3=Load Loss 1 | 3 | Level Current | Configuration | Set(1) | REAL | Defines the monitoring level in terms of output current to the motor (assuming current is proportional to power being applied to the load). | 0.0…30.0 A(2)
0x0434 (1076) | Load Monitor | 1=Shear Pin 1 2=Shear Pin 2 3=Load Loss 1 | 5 | Time | Configuration | Set(1) | REAL |  | 0.0…30.0 seconds
0x0434 (1076) | Load Monitor | 1=Shear Pin 1 2=Shear Pin 2 3=Load Loss 1 | 100 | Tripped | Status | Get | BOOL | Indicates whether load monitoring has detected power output above or below the configured level. | 0=Load monitoring has not detected power output different than the configured level. 1=Load monitoring has detected power output that is above or below the configured level.
0x0435 (1077) | Slip Droop Compensation | 1=Slip Droop Compensation 1 | 2 | Mode | Status | Get | USINT | Indicates the mode in which the slip droop compensation object is currently operating. | 0=Disabled: No slip or droop compensation is being performed. The output attribute (3)is forced to 0.0. 1=Enabled, Using Estimated Slip Droop: Slip or droop compensation is being performed. The output attribute (3) is being set to an estimated value based on configuration values and measured load (open loop control) . 2=Enabled, Using Measured Slip Droop: Slip or droop compensation is being performed. The output attribute (3) is being set to a measured amount of slip or droop based on input from a feedback device (closed loop control).
0x0435 (1077) | Slip Droop Compensation | 1=Slip Droop Compensation 1 | 3 | Output | Status | Get | REAL | Indicates the current amount of slip or droop that the compensation feature is requesting be added to the output frequency going to the motor. This is output is either an estimate or measured amount of slip or droop (in revolutions per minute). Positive values indicate slip compensation is being requested (increased frequency to account for slip). Negative values indicate droop compensation is being requested (decreased frequency). | —
0x0435 (1077) | Slip Droop Compensation | 1=Slip Droop Compensation 1 | 4 | Full Load Slip Droop Default | Status | Get | REAL | When slip or droop is being estimated, this value is the default amount of slip or droop that is applied when the motor is under full load. Positive values indicate slip compensation; negative values indicate droop compensation. | —
0x0435 (1077) | Slip Droop Compensation | 1=Slip Droop Compensation 1 | 5 | Full Load Slip Droop User | Configuration | Set(1) | REAL | When slip or droop is being estimated, this value defines the amount of slip or droop that is applied when the motor is under full load. Positive values indicate slip compensation; negative values indicate droop compensation. Valid values depend on the user-configured value for the Poles attribute (7) of the Motor Configuration object (0x041D). | (-1200 ÷ number of motor poles) … (1200 ÷ number of motor poles) rpm Default=0 rpm
0x0435 (1077) | Slip Droop Compensation | 1=Slip Droop Compensation 1 | 6 | Full Load Slip Droop Total | Status | Get | REAL | When slip or droop is being estimated, this value is the total amount of slip or droop that is applied when the motor is under full load. This is the sum of the default and user configured slip or droop compensation values. Positive values indicate slip compensation; negative values indicate droop compensation. | —
0x0435 (1077) | Slip Droop Compensation | 1=Slip Droop Compensation 1 | 7 | Disable At Zero Speed | Configuration | Set(1) | BOOL | Disables any slip or droop compensation from occurring when the motor speed is zero | 0=Slip or droop compensation is not disabled when the motor is at zero speed. (default) 1= Slip or droop compensation is disabled when the motor is at zero speed. The output attribute (3) is forced to 0.0 when the commmanded speed in the associated Velocity Control Supervisor (0x041e) instance is 0 and the motor is operating at zero speed.
-1 | Configuration attributes are settable through the user interface of the configuration software. If changes are made by using another method, the changed values may be overwritten when a connection is re-established or the device is power cycled.
-2 | The Attribute values listed are for the full range of Armor PowerFlex drives. The valid range for your catalog number is shown in the user interface of the Logix Designer application, where you configure your drive.

## FaultAlarmEvent Objects
Armor PowerFlex CIP Object Definitions
For more information see:
Armor PowerFlex AC Drives User Manual, publication 35-UM001.
Class | Name | Instance | Attribute | Attribute Name | Data Classification | Access Rule | Data Type | Description | Attribute Values
0x0417 (1047) | Fault Alarm | 1=Fault Alarm | 3 | Highest Severity | Status | Get | USINT | Indicates the highest severity of the fault(s) that have not been acknowledged or alarm(s) that are active. | 0=No unacknowledged faults or active alarms. 4= Event 6=Major Alarm 8=Major Fault See the Troubleshooting chapter in the user manual for more information.
0x0417 (1047) | Fault Alarm | 1=Fault Alarm | 4 | Fault Count | Status | Get | UDINT | Indicates the number of unacknowledged fault entries. | —
0x0417 (1047) | Fault Alarm | 1=Fault Alarm | 5 | Alarm Count | Status | Get | UDINT | Indicates the number of active alarm entries. | —
0x0417 (1047) | Fault Alarm | 1=Fault Alarm | 8 | Faulted | Status | Get | BOOL | Indicates whether there is at least one unacknowledged fault. | 0=No unacknowledged faults exist 1=One or more unacknowledged faults exist.
0x0417 (1047) | Fault Alarm | 1=Fault Alarm | 9 | Alarm Active | Status | Get | BOOL | Indicates whether there is at least one active alarm. | 0=No alarms are active 1=One or more alarms are active.
0x0417 (1047) | Fault Alarm | 1=Fault Alarm | 10 | Trip Fault Event Type Code | Status | Get | UDINT | Indicates the event type code of the fault event that caused the last trip or transition to the faulted state. This attribute is set to 0 when the trip fault entry is cleared. The Trip Fault Log Entry ID attribute (6) provides more information on the fault. | —
0x0417 (1047) | Fault Alarm | 1=Fault Alarm | 11 | Maximum Fault Count | Constant | Get | UDINT | Indicates the maximum number of unacknowledged faults the device can save in the queue. If more unique unacknowledged faults occur, they are not recorded. | 10
0x0417 (1047) | Fault Alarm | 1=Fault Alarm | 12 | Maximum Alarm Count | Constant | Get | UDINT | Indicates the maximum number of active alarms the device can save in the queue. If more unique active alarms occur, they are not recorded. | 10

## Feedback Objects
Armor PowerFlex CIP Object Definitions
For more information see:
Armor PowerFlex AC Drives User Manual, publication 35-UM001.
Class | Name | Instance | Attribute | Attribute Name | Data Classification | Access Rule | Data Type | Description | Attribute Values
0x042F (1071) | Feedback | 1=Feedback | 1 | Data Valid | Status | Get | BOOL | Indicates whether the data that is being reported in the status attributes for this instance are valid for use. | 0=Feedback data is not being received or a feedback fault exists. 1=Feedback data is being received and processed by the feedback device with no feedback faults.
0x042F (1071) | Feedback | 1=Feedback | 2 | Position | Status | Get | UDINT | Indicates the position measured by the feedback device, in raw counts (unscaled) that are reported by the device. | —
0x042F (1071) | Feedback | 1=Feedback | 3 | Velocity | Status | Get | REAL | Indicates the velocity measured by the device. Units are revolutions per second for rotary encoders and millimeters per second for linear encoders. Direction of motion is indicated by the sign of the velocity value. | —
0x042F (1071) | Feedback | 1=Feedback | 5 | Fault | Status | Get | BOOL | Indicates whether the feedback device is in a faulted state. When in a faulted state, the value of all status attributes except Data Valid (1) is not determined. | —
0x042F (1071) | Feedback | 1=Feedback | 6 | Fault Type | Status | Get | UINT | If a feedback device is in a faulted state, this indicates the type or reason for the fault. | 0=No Fault 1=Signal Loss: A fault occurred because a feedback signal is missing, shorted, or open. 2=Data Loss: A fault occurred because data could not be obtained from a feedback device. This is typically reported when there is a problem with the data communications channel to the encoder. 3=Signal Diagnostic: A fault occurred because a diagnostic on one or more feedback signals failed. This may indicate electrical noise is corrupting the feedback signals, or another transient problem with the feedback signals. 4=Velocity Comparison Diagnostic: A fault occurred because a diagnostic on feedback velocity detected too great of a difference between the velocity determined by the encoder and the predicted or estimated velocity based on the motor control model.
0x042F (1071) | Feedback | 1=Feedback | 100 | Enable | Configuration | Set(1) | BOOL | Enables or disables the feedback device. | 0=Feedback device is disabled. No status updates, faults or events are generated by this instance. (default) 1=Feedback device is enabled.
0x042F (1071) | Feedback | 1=Feedback | 101 | Interface Type | Configuration | Set(1) | USINT | Defines the type of electrical interface to the feedback device. | 0=Not Specified: Encoder type is unknown or undefined. (default) 1=Digital Incremental, AqB Dual Channel, Differential: A quadrature encoder with 4 square-wave (digital) feedback signals, which are A, A', B, B'. 4=Generic Sine/Cosine: A generic analog sine/cosine encoder whose feedback signals are 1 volt peak to peak sine waves. 6=Hiperface Sine/Cosine: A Hiperface digital encoder with a separate analog sine/cosine interface. 7=EnDat Sine/Cosine: An EnDat digital encoder with a separate analog sine/cosine interface. 128=Digital Incremental, AqB Dual Channel, Single Ended: A quadrature encoder with 2 square-wave (digital) feedback signals, which are A, B. 129=Digital Incremental, Single Channel, Differential: An encoder with 2 square-wave (digital) feedback signals, which are A, A'. 130=Digital Incremental, Single Channel, Single Ended: An encoder with 1 square wave (digital) feedback signal, which is A.
0x042F (1071) | Feedback | 1=Feedback | 105 | Cycle Resolution | Configuration | Set(1) | UDINT | Defines the resolution of the feedback device, in the number of cycles per fixed amount of travel. | 1…20,000 cycles Default=1024 cycles
0x042F (1071) | Feedback | 1=Feedback | 106 | Cycle Interpolation | Status | Get | UDINT | Indicates the number of counts that can be interpolated out of one feedback cycle. | 0
0x042F (1071) | Feedback | 1=Feedback | 108 | Polarity | Configuration | Set(1) | USINT | Lets the direction of motion reported by the feedback device be inverted to match actual direction of motion. | 0=Normal (default) 1=Inverted
0x042F (1071) | Feedback | 1=Feedback | 109 | Velocity Comparison Diagnostic Enable | Configuration | Set(1) | BOOL | Enables a diagnostic that detects and faults the feedback device if the feedback velocity is too different from the predicted velocity. This diagnostic may not be suitable and may cause faults for certain applications, such as high inertia or positioning. | 0=Diagnostic is disabled. (default) 1=Diagnostic is enabled.
-1 | Configuration attributes are settable through the user interface of the configuration software. If changes are made by using another method, the changed values may be overwritten when a connection is re-established or the device is power cycled.

## Inverter Objects
Armor PowerFlex CIP Object Definitions
For more information see:
Armor PowerFlex AC Drives User Manual, publication 35-UM001.
Class | Name | Instance | Attribute | Attribute Name | Data Classification | Access Rule | Data Type | Description | Attribute Values
0x0424 | DC Bus | 1=DC Bus | 1 | Type | Constant | Get | UDINT | Indicates the type of DC bus that this object represents. | 0=Passive (Diode) Front End: A DC bus that is created by rectifying AC line voltage via a passive diode based rectifier.
0x0424 | DC Bus | 1=DC Bus | 2 | Measured Voltage | Status | Get | REAL | Indicates the current voltage being measured on the DC bus. The reported value may have some filtering applied so that this value may not reflect an instantaneous voltage. | —
0x0424 (1060) | DC Bus | 1=DC Bus | 3 | Ripple Voltage | Status | Get | REAL | Indicates the magnitude of the ripple or variation of the voltage of the DC bus measured over time. | —
0x0424 (1060) | DC Bus | 1=DC Bus | 104 | Voltage Low Limit Soft | Configuration | Set(1) | REAL | Defines a user-configurable or soft lower limit on the voltage of the DC bus, below which an Undervoltage, Soft fault is declared. | 390 V (default) 260 V
0x0424 (1060) | DC Bus | 1=DC Bus | 106 | Bus Regulator Enable | Configuration | Set(1) | BOOL | Turns active regulation of the DC bus voltage on or off. When it is enabled, the DC bus voltage is actively maintained at the nominal voltage. | 0=DC bus voltage regulation disabled 1=DC bus voltage regulation enabled (default)
0x0424 (1060) | DC Bus | 1=DC Bus | 107 | Ripple Voltage High Limit Hard | Constant | Get | REAL | Indicates the fixed or hard upper limit which defines the maximum ripple voltage allowed on the DC bus, above which an Ripple Voltage Over Limit, Hard fault is declared. | 58.6V
0x0425 (1061) | Inverter | 1=Inverter | 1 | Output Frequency | Status | Get | REAL | Indicates the current frequency (in Hertz) of the AC output from the inverter. All output phases have the same output frequency. | —
0x0425 (1061) | Inverter | 1=Inverter | 2 | Output Voltage | Status | Get | REAL | Indicates the current voltage RMS (in Volts) of the AC output from the inverter. All output phases will have the same output voltage. | —
0x0425 (1061) | Inverter | 1=Inverter | 3 | Output Current Total | Status | Get | REAL | Indicates the total output current (in Amps) of the inverter. If there are multiple phases, this is the average current of all the phases. | —
0x0425 (1061) | Inverter | 1=Inverter | 4 | Output Power | Status | Get | REAL | Indicates the current output power (in kilowatts) of the inverter. If there are multiple phases, this is the sum of power being output on all phases. | —
0x0425 (1061) | Inverter | 1=Inverter | 6 | Torque Current | Status | Get | REAL | Indicates the amount of torque producing current (in Amps) of the inverter. | —
0x0425 (1061) | Inverter | 1=Inverter | 7 | Output Power Factor | Status | Get | REAL | Indicates the ratio of the output power of the inverter to the input power, providing a measure of the efficiency of the inverter. | —
0x0425 (1061) | Inverter | 1=Inverter | 8 | Output Current, Unfiltered | Status | Get | REAL | Indicates the unfiltered output RMS current (in Amps) of the inverter . | —
0x0425 (1061) | Inverter | 1=Inverter | 30 | Rated Output Frequency | Status | Get | REAL | Indicates the rated output frequency (in Hertz) for the inverter, which is the maximum frequency that the inverter can output. | 500.0 Hz
0x0425 (1061) | Inverter | 1=Inverter | 31 | Rated Output Voltage | Status | Get | REAL | Indicates the rated output voltage for the inverter. This value is typically the maximum value for continuous operation. | 460.0V
0x0425 (1061) | Inverter | 1=Inverter | 32 | Rated Output Current | Status | Get | REAL | Indicates the rated total output current (in Amps)for the inverter. This value is typically the maximum value for continuous operation. | —
0x0425 (1061) | Inverter | 1=Inverter | 33 | Rated Output Power | Status | Get | REAL | Indicates the rated output power for the inverter. This value is typically the maximum value for continuous operation. | —
0x0425 (1061) | Inverter | 1=Inverter | 34 | Number Of Phases | Status | Get | USINT | Indicates the number of output phases produced by the inverter. | 3
0x0425 (1061) | Inverter | 1=Inverter | 50 | Max PWM Carrier Frequency | Configuration | Set(1) | REAL | This is the configured maximum PWM carrier frequency used for switching the output devices on and off to form the output waveform. | 2000.0…16000.0 Hz (default = 4000.0)
0x0425 (1061) | Inverter | 1=Inverter | 51 | Actual PWM Carrier Frequency | Status | Get | REAL | This is the actual PWM carrier frequency used for switching the output devices on and off to form the output waveform. | —
0x0425 (1061) | Inverter | 1=Inverter | 55 | Minimum Output Frequency | Configuration | Set(1) | REAL | Configures the minimum frequency (in Hertz) of the AC output from the inverter. | 0…500 Hz (default = 0.0)
0x0425 (1061) | Inverter | 1=Inverter | 56 | Maximum Output Frequency | Configuration | Set(1) | REAL | Configures the maximum frequency (in Hertz) of the AC output from the inverter. | 0…500 Hz (default = 60.0)
0x0436 (1078) | Inverter Protection | 1=Inverter Protection 1 | 107 | Overload Action Enable, Reduce Current Limit | Configuration | Set(1) | BOOL | Enables the use of a current limit instead of faulting the device when an overload occurs or is imminent. The current limit is equal to the rated current of the device. | 0=Current limit overload action is disabled. (default) 1=Current limit overload action is enabled.
0x0436 (1078) | Inverter Protection | 1=Inverter Protection 1 | 109 | Overload Action Enable, Reduce PWM Frequency | Configuration | Set(1) | BOOL | Enables the reduction of the PWM output carrier frequency instead of faulting the device when an overload occurs or is imminent. A reduction in the PWM frequency typically occurs only in thermal overload conditions because it has little to no effect on actual output current. | 0=PWM frequency reduction overload action is disabled. (default) 1=PWM frequency reduction overload action is enabled.
0x0436 (1078) | Inverter Protection | 1=Inverter Protection 1 | 200 | Active Source | Status | Get | UINT | Indicates the instance number of Inverter Current Limit Source object (0x0437) instance currently being used to supply the user defined current limit. IMPORTANT: Even if there is no active source, a current limit can still be applied automatically based on the overload actions selected. | 1=Preset 1 2=Preset 2
0x0436 (1078) | Inverter Protection | 1=Inverter Protection 1 | 201 | Current Limit | Status | Get | REAL | Indicates the value (in Amps) of the active current limit in use, if any. The value of this attribute may come from a user-defined current limit, via attribute 100 of Inverter Current Limit Source object (0x0437). Or, the value may be forced to a value if Overload Action Enable, Reduce Current Limit (attribute 107) is set to true (1). | See Description.
0x0436 (1078) | Inverter Protection | 1=Inverter Protection 1 | 203 | Current Limiting Occurring | Status | Get | BOOL | Indicates whether the output current has exceeded the Current Limit attribute (101) value and steps have been taken to reduce the output current. | 0=Output current is below the value of the Current Limit attribute (101). 1=Output current has exceeded the Current Limit attribute (101) value. Current limiting is active.
0x0437 (1079) | Inverter Current Limit Source | 1=Preset 1 | 1 | Enable | Constant | Get | BOOL | Indicates that the source is enabled and can become operational. | 1=Source is enabled and can become the active source.
|  | 2=Preset 2 | 1 | Enable | Configuration | Set(1) | BOOL | Lets the source be enabled or disabled. When enabled, the source can become operational. | 0=Source is disabled. (default) 1=Source is enabled.
0x0437 (1079) | Inverter Current Limit Source | 1=Preset 1 | 2 | Inhibit | Constant | Get | BOOL | Indicates that the source is not inhibited. | 0=Source is not inhibited and can become the active source.
|  | 2=Preset 2 | 2 | Inhibit | Control | Set | BOOL | Lets the source be inhibited and temporarily disabled (ignored). While inhibited, it cannot become the active control source. | 0=Source is not inhibited and can become the active source. 1=Source is inhibited.
0x0437 (1079) | Inverter Current Limit Source | 1=Preset 1 2=Preset 2 | 3 | Operational | Status | Get | BOOL | Indicates whether the source instance is currently operational. | 0=Source is not operating and cannot become the active source. 1=Source is operating and can become the active source.
0x0437 (1079) | Inverter Current Limit Source | 1=Preset 1 2=Preset 2 | 5 | Priority | Constant | Get | UINT | Indicates the order in which multiple operational sources are considered when a single active source needs to be determined. Higher values mean greater priority in the active source determination. If two values share the same priority value, priority is determined by instance number (lowest instance number has highest priority). | For Preset 1 instance (1)=50 For Preset 2 instance (2)=60
0x0437 (1079) | Inverter Current Limit Source | 1=Preset 1 2=Preset 2 | 100 | Current Limit | Configuration | Set(1) | REAL | Defines the current limit value (in Amps) to be enforced by the Inverter Protection object (0x0465); sets an upper limit on inverter output current. | 0.0…10.8 A(2) Default=9.0 A
-1 | Configuration attributes are settable through the user interface of the configuration software. If changes are made by using another method, the changed values may be overwritten when a connection is re-established or the device is power cycled.
-2 | The Attribute values listed are for the full range of Armor PowerFlex drives. The valid range for your catalog number is shown in the user interface of the Logix Designer application, where you configure your drive.

## Motor Objects
Armor PowerFlex CIP Object Definitions
For more information see:
Armor PowerFlex AC Drives User Manual, publication 35-UM001.
Class | Name | Instance | Attribute | Attribute Name | Data Classification | Access Rule | Data Type | Description | Attribute Values
0x041D | Motor Configuration | 1=motor | 1 | Type | Configuration | Set(1) | USINT | Indicates the motor technology used. | 2=AC Rotary Induction
0x041D | Motor Configuration | 1=motor | 3 | Voltage | Configuration | Set(1) | REAL | Defines the motor nameplate (rated) voltage. | 20.0…460.0V Default=460.0
0x041D (1053) | Motor Configuration | 1=motor | 4 | Current | Configuration | Set(1) | REAL | Defines the motor nameplate (rated) current or full load amps (FLA), indicating the total current draw at full load and speed. | 0.1…12.0 A(2)
0x041D (1053) | Motor Configuration | 1=motor | 6 | Rated Power | Configuration | Set(1) | REAL | Defines the motor nameplate (rated) output power (in kW), indicating the maximum power produced by the motor at the rated voltage and frequency. | 0.0…2.238 kW(2)
0x041D (1053) | Motor Configuration | 1=motor | 7 | Poles | Configuration | Set(1) | UINT | Defines the motor nameplate poles, indicating the number of poles in a rotary motor (poles per revolution). This value is always an even number, as poles always exist in pairs. | 2…40 Default=4
0x041D (1053) | Motor Configuration | 1=motor | 8 | Rated Speed | Configuration | Set(1) | REAL | Defines the motor nameplate (rated) speed of a rotary motor, indicating the speed of the motor under rated conditions. For PM motors, this is generally specified at rated voltage based on either rated current, rated torque, or rated power. For induction motors this value is the speed of the motor driven at rated frequency under rated torque load. This value is synonymous with the term base speed. | 0.0…24000.0 rpm Default=1750.0 rpm
0x041D (1053) | Motor Configuration | 1=motor | 9 | Rated Frequency | Configuration | Set(1) | REAL | Defines the motor nameplate (rated) frequency (in Hz). | 15.0…500.0 Hz
0x041D (1053) | Motor Configuration | 1=motor | 10 | Polarity | Configuration | Set(1) | USINT | Lets the direction of motion be inverted. | 0=Normal (default) 1=Inverted
0x041D (1053) | Motor Configuration | 1=motor | 100 | Im Stator Resistance | Status | Get | REAL | Indicates the Y-circuit, phase-neutral, winding resistance (in Ohms) of the stator as shown as R1 in the IEEE motor model. The value of this attribute comes from a Motor Tuning Data Source instance. See the user manual for more information. | —
0x041D (1053) | Motor Configuration | 1=motor | 101 | Im Stator Resistance Source | Configuration | Set(1) | UDINT | Defines the source instance of the IM Stator Resistance attribute (100) value. | 1=Use Default instance value. (default) 3=Use Autotune Saved value. 4=User-defined manually entered value.
0x041D (1053) | Motor Configuration | 1=motor | 102 | Im Rotor Resistance | Status | Get | REAL | Indicates the phase-neutral equivalent stator-referenced winding resistance (in Ohms) of the rotor as shown as R2 in the IEEE motor model. | —
0x041D (1053) | Motor Configuration | 1=motor | 103 | Im Rotor Resistance Source | Configuration | Set(1) | UDINT | Defines the source instance of the IM Rotor Resistance attribute (102) value. The value of this attribute comes from a Motor Tuning Data Source instance. | 1=Use Default instance value. (default) 3=Use Autotune Saved value. 4=User-defined manually entered value.
0x041D (1053) | Motor Configuration | 1=motor | 104 | Im Flux Current | Status | Get | REAL | Indicates the Id Current Reference (in Amps) that is required to generate full motor flux. The value of this attribute comes from a Motor Tuning Data Source instance. This value is closely approximated by the No Load Motor Rated Current commonly found in Induction Motor data sheets. | —
0x041D (1053) | Motor Configuration | 1=motor | 105 | Im Flux Current Source | Configuration | Set(1) | UDINT | Defines the source instance of the IM Flux Current attribute (104) value. | 1=Use Default instance value. (default) 3=Use Autotune Saved value. 4=User-defined manually entered value.
0x041D (1053) | Motor Configuration | 1=motor | 110 | Im Total Leakage Inductance | Status | Get | REAL | Indicates the total leakage inductance value (stator leakage plus rotor leakage) (in H) for the motor. The value of this attribute comes from a Motor Tuning Data Source instance. | —
0x041D (1053) | Motor Configuration | 1=motor | 111 | Im Total Leakage Inductance Source | Configuration | Set(1) | UDINT | Defines the source instance of the IM Total Leakage Inductance attribute (110) value. | 1=Use Default instance value. (default) 3=Use Autotune Saved value. 4=User-defined manually entered value.
0x041D (1053) | Motor Configuration | 1=motor | 112 | Im Mutual Inductance | Status | Get | REAL | Indicates the mutual inductance value (in H) for the motor. The value of this attribute comes from a Motor Tuning Data Source instance. | —
0x041D (1053) | Motor Configuration | 1=motor | 113 | Im Mutual Inductance Source | Configuration | Set(1) | UDINT | Defines the source instance of the IM Mutual Inductance attribute (112) value. | 1=Use Default instance value. (default) 3=Use Autotune Saved value. 4=User-defined manually entered value.
0x041D (1053) | Motor Configuration | 1=motor | 150 | Pm Motor Resistance | Status | Get | REAL | Indicates the phase to phase or stator resistance (in Ohms) of a permanent magnet motor. The value of this attribute comes from a Motor Tuning Data Source instance | —
0x041D (1053) | Motor Configuration | 1=motor | 151 | Pm Motor Resistance Source | Configuration | Set(1) | UDINT | Defines the source instance of the Permanent Magnet Motor Resistance attribute (150) value. | 1=Use Default instance value. (default) 3=Use Autotune Saved value. 4=User-defined manually entered value.
0x041D (1053) | Motor Configuration | 1=motor | 152 | Pm Motor Lq Inductance | Status | Get | REAL | Indicates the phase-neutral, q-axis, inductance (in H) of a permanent magnet motor. For surface permanent magnet motors, the Lq and Ld inductances are the same or similar. For SPM motors, both these attributes can be set to the same values. The value of this attribute comes from a Motor Tuning Data Source instance. | —
0x041D (1053) | Motor Configuration | 1=motor | 153 | Pm Motor Lq Inductance Source | Configuration | Set(1) | UDINT | Defines the source instance of the Permanent Magnet Motor Lq Inductance attribute (152) value. | 1=Use Default instance value. (default) 3=Use Autotune Saved value. 4=User-defined manually entered value.
0x041D (1053) | Motor Configuration | 1=motor | 154 | Pm Motor Ld Inductance | Status | Get | REAL | Indicates the phase-neutral, d-axis, inductance (in H) of a permanent magnet motor. For surface permanent magnet motors, the Lq and Ld inductances are the same or similar. For SPM motors, both these attributes can be set to the same values. The value of this attribute comes from a Motor Tuning Data Source instance. | —
0x041D (1053) | Motor Configuration | 1=motor | 155 | Pm Motor Ld Inductance Source | Configuration | Set(1) | UDINT | Defines the source instance of the Permanent Magnet Motor Ld Inductance attribute (154) value. | 1=Use Default instance value. (default) 3=Use Autotune Saved value. 4=User-defined manually entered value.
0x041D (1053) | Motor Configuration | 1=motor | 156 | Pm Motor Rotary Voltage Constant | Status | Get | REAL | Indicates the voltage, or back-EMF, constant of a rotary permanent magnet motor in volts (RMS) at the motor rated speed. It is assumed the back-EMF from the motor is sinusoidal. The value of this attribute comes from a Motor Tuning Data Source instance. | —
0x041D (1053) | Motor Configuration | 1=motor | 157 | Pm Motor Rotary Voltage Constant Source | Configuration | Set(1) | UDINT | Defines the source instance of the Permanent Magnet Motor Rotary Voltage Constant attribute (156) value. | 1=Use Default instance value. (default) 3=Use Autotune Saved value. 4=User-defined manually entered value.
0x041D (1053) | Motor Configuration | 1=motor | 200 | Autotune Ready | Status | Get | BOOL | Indicates whether the device is ready to perform an autotune operation. | 0=Device is not ready 1=Device is ready
0x041D (1053) | Motor Configuration | 1=motor | 201 | Autotune Active | Status | Get | BOOL | Indicates whether an autotune operation is in progress (active). | 0=Autotune is not in progress 1=Autotune is in progress
0x041D (1053) | Motor Configuration | 1=motor | 202 | Autotune Status | Status | Get | UINT | Provides status information about the current or last autotune operation. | 0=No Status: No autotune operations have been performed since the last power-cycle. 1=In Progress: Autotune operation is currently running. 2=Completed Successfully 3=Failed, General: Last autotune operation failed with no specific information on the cause of the failure. 4=Failed, Aborted: The last autotune operation failed because it was aborted by the user. 5=Failed, Fault: The last autotune operation failed because another fault occurred during the tuning. 6=Failed, Invalid Measurement: The last autotune operation failed because the measured value for a motor tuning parameter was invalid. 7=Failed, Excessive Load: The last autotune operation failed because the load was too great to allow the motor to come up to speed during the tuning operation. The Autotune Torque Limit attribute may be set too low for the load. 8=Failed, Position Limit: The last autotune operation could not move the motor sufficiently to obtain tuning data due to the Autotune Position Limit setting.
0x041D (1053) | Motor Configuration | 1=motor | 203 | Autotune Operation Type Active | Status | Get | USINT | Indicates the type of operation being performed when an autotune operation is active. | 0=No Operation: No autotune operation is in progress 1=Static 2=Rotate 3=Inertia
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 100 | Im Stator Resistance | Constant | Get | REAL | Indicates the Y circuit, phase-neutral, winding resistance of the stator as shown as R1 in the IEEE motor model. | 3.29 Ohms
|  | 2=Autotune Result | 100 | Im Stator Resistance | Status | Get | REAL | Indicates the Y circuit, phase-neutral, winding resistance of the stator as shown as R1 in the IEEE motor model. | 0.0…7.5 Ohms
|  | 3=Autotune Saved 4=User-specified | 100 | Im Stator Resistance | Configuration | Set(1) | REAL | Indicates the Y circuit, phase-neutral, winding resistance of the stator as shown as R1 in the IEEE motor model. | 0.0…7.5 Ohms
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 101 | Im Stator Resistance State | Constant | Get | USINT | Indicates the state of the Induction Motor Stator Resistance attribute (100) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set
|  | 2=Autotune Result | 101 | Im Stator Resistance State | Status | Get | USINT | Indicates the state of the Induction Motor Stator Resistance attribute (100) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set (default) 1=Invalid, Measurement Failed: An attempt was made to measure the value of the attribute, but it failed. 2=Valid, Calculated 3=Valid, User Supplied 4=Valid, Measured
|  | 3=Autotune Saved 4=User-specified | 101 | Im Stator Resistance State | Configuration | Set(1) | USINT | Indicates the state of the Induction Motor Stator Resistance attribute (100) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set (default) 1=Invalid, Measurement Failed: An attempt was made to measure the value of the attribute, but it failed. 2=Valid, Calculated 3=Valid, User Supplied 4=Valid, Measured
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 102 | Im Rotor Resistance | Constant | Get | REAL | Indicates the phase-neutral equivalent stator-referenced winding resistance of the rotor (in Ohms) as shown as R2 in the IEEE motor model. | 10.0 Ohms
|  | 2=Autotune Result | 102 | Im Rotor Resistance | Status | Get | REAL | Indicates the phase-neutral equivalent stator-referenced winding resistance of the rotor (in Ohms) as shown as R2 in the IEEE motor model. | 0.0…655.35 Ohms Default=10.0 Ohms
|  | 3=Autotune Saved 4=User-specified | 102 | Im Rotor Resistance | Configuration | Set(1) | REAL | Indicates the phase-neutral equivalent stator-referenced winding resistance of the rotor (in Ohms) as shown as R2 in the IEEE motor model. | 0.0…655.35 Ohms(2) Default=10.0 Ohms
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 103 | Im Rotor Resistance State | Constant | Get | USINT | Indicates the state of the Induction Motor Rotor Resistance attribute (102) value; that is whether it is valid and how the value was determined. | 0=Invalid, Not Set
|  | 2=Autotune Result | 103 | Im Rotor Resistance State | Status | Get | USINT | Indicates the state of the Induction Motor Rotor Resistance attribute (102) value; that is whether it is valid and how the value was determined. | 0=Invalid, Not Set (default) 1=Invalid, Measurement Failed: An attempt was made to measure the value of the attribute, but it failed. 2=Valid, Calculated 3=Valid, User Supplied 4=Valid, Measured
|  | 3=Autotune Saved 4=User-specified | 103 | Im Rotor Resistance State | Configuration | Set(1) | USINT | Indicates the state of the Induction Motor Rotor Resistance attribute (102) value; that is whether it is valid and how the value was determined. | 0=Invalid, Not Set (default) 1=Invalid, Measurement Failed: An attempt was made to measure the value of the attribute, but it failed. 2=Valid, Calculated 3=Valid, User Supplied 4=Valid, Measured
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 104 | Im Flux Current | Constant | Get | REAL | Indicates the Id Current Reference (in Amps) that is required to generate full motor flux. This value is closely approximated by the No Load Motor Rated Current commonly found in Induction Motor data sheets. | 1.957 A
|  | 2=Autotune Result | 104 | Im Flux Current | Status | Get | REAL | Indicates the Id Current Reference (in Amps) that is required to generate full motor flux. This value is closely approximated by the No Load Motor Rated Current commonly found in Induction Motor data sheets. | 0.0…8.4 A
|  | 3=Autotune Saved 4=User-specified | 104 | Im Flux Current | Configuration | Set(1) | REAL | Indicates the Id Current Reference (in Amps) that is required to generate full motor flux. This value is closely approximated by the No Load Motor Rated Current commonly found in Induction Motor data sheets. | 0.0…8.4 A(2)
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 105 | Im Flux Current State | Constant | Get | USINT | Indicates the state of the Induction Motor Flux Current attribute (104) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set
|  | 2=Autotune Result | 105 | Im Flux Current State | Status | Get | USINT | Indicates the state of the Induction Motor Flux Current attribute (104) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set (default) 1=Invalid, Measurement Failed: An attempt was made to measure the value of the attribute, but it failed. 2=Valid, Calculated 3=Valid, User Supplied 4=Valid, Measured
|  | 3=Autotune Saved 4=User-specified | 105 | Im Flux Current State | Configuration | Set(1) | USINT | Indicates the state of the Induction Motor Flux Current attribute (104) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set (default) 1=Invalid, Measurement Failed: An attempt was made to measure the value of the attribute, but it failed. 2=Valid, Calculated 3=Valid, User Supplied 4=Valid, Measured
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 110 | Im Total Leakage Inductance | Constant | Get | REAL | Indicates the total leakage inductance (in H) of the motor, which includes both rotor leakage inductance and stator leakage inductance. | 0.0 H
|  | 2=Autotune Result | 110 | Im Total Leakage Inductance | Status | Get | REAL | Indicates the total leakage inductance (in H) of the motor, which includes both rotor leakage inductance and stator leakage inductance. | 0.0…6553.5 H
|  | 3=Autotune Saved 4=User-specified | 110 | Im Total Leakage Inductance | Configuration | Set(1) | REAL | Indicates the total leakage inductance (in H) of the motor, which includes both rotor leakage inductance and stator leakage inductance. | 0.0…6553.5 H
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 111 | Im Total Leakage Inductance State | Constant | Get | USINT | Indicates the state of the Induction Motor Total Leakage Inductance attribute (110) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set
|  | 2=Autotune Result | 111 | Im Total Leakage Inductance State | Status | Get | USINT | Indicates the state of the Induction Motor Total Leakage Inductance attribute (110) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set (default) 1=Invalid, Measurement Failed: An attempt was made to measure the value of the attribute, but it failed. 2=Valid, Calculated 3=Valid, User Supplied 4=Valid, Measured
|  | 3=Autotune Saved 4=User-specified | 111 | Im Total Leakage Inductance State | Configuration | Set(1) | USINT | Indicates the state of the Induction Motor Total Leakage Inductance attribute (110) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set (default) 1=Invalid, Measurement Failed: An attempt was made to measure the value of the attribute, but it failed. 2=Valid, Calculated 3=Valid, User Supplied 4=Valid, Measured
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 112 | Im Mutual Inductance | Constant | Get | REAL | Indicates the mutual inductance (in H)of the motor. | 0.0 H
|  | 2=Autotune Result | 112 | Im Mutual Inductance | Status | Get | REAL | Indicates the mutual inductance (in H)of the motor. | 0.0…6553.5 H
|  | 3=Autotune Saved 4=User-specified | 112 | Im Mutual Inductance | Configuration | Set(1) | REAL | Indicates the mutual inductance (in H)of the motor. | 0.0…6553.5 H
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 113 | Im Mutual Inductance State | Constant | Get | USINT | Indicates the state of the Induction Motor Mutual Inductance attribute (112) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set
|  | 2=Autotune Result | 113 | Im Mutual Inductance State | Status | Get | USINT | Indicates the state of the Induction Motor Mutual Inductance attribute (112) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set (default) 1=Invalid, Measurement Failed: An attempt was made to measure the value of the attribute, but it failed. 2=Valid, Calculated 3=Valid, User Supplied 4=Valid, Measured
|  | 3=Autotune Saved 4=User-specified | 113 | Im Mutual Inductance State | Configuration | Set(1) | USINT | Indicates the state of the Induction Motor Mutual Inductance attribute (112) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set (default) 1=Invalid, Measurement Failed: An attempt was made to measure the value of the attribute, but it failed. 2=Valid, Calculated 3=Valid, User Supplied 4=Valid, Measured
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 150 | Pm Motor Resistance | Constant | Get | REAL | Indicates the phase to phase or stator resistance (in Ohms) of a permanent magnet motor. | 115.0 Ohms
|  | 2=Autotune Result | 150 | Pm Motor Resistance | Status | Get | REAL | Indicates the phase to phase or stator resistance (in Ohms) of a permanent magnet motor. | —
|  | 3=Autotune Saved 4=User-specified | 150 | Pm Motor Resistance | Configuration | Set(1) | REAL | Indicates the phase to phase or stator resistance (in Ohms) of a permanent magnet motor. | 0.0…6553.5 Ohms
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 151 | Pm Motor Resistance State | Constant | Get | USINT | Indicates the state of the Permanent Magnet Motor Resistance attribute (150) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set
|  | 2=Autotune Result | 151 | Pm Motor Resistance State | Status | Get | USINT | Indicates the state of the Permanent Magnet Motor Resistance attribute (150) value; that is, whether it is valid and how the value was determined. | —
|  | 3=Autotune Saved 4=User-specified | 151 | Pm Motor Resistance State | Configuration | Set(1) | USINT | Indicates the state of the Permanent Magnet Motor Resistance attribute (150) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set (default) 1=Invalid, Measurement Failed: An attempt was made to measure the value of the attribute, but it failed. 2=Valid, Calculated 3=Valid, User Supplied 4=Valid, Measured
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 152 | Pm Motor Lq Inductance | Constant | Get | REAL | Indicates the phase-neutral, q-axis, inductance (in H) of a permanent magnet motor. For surface permanent magnet motors, the Lq and Ld inductances are the same or similar. For SPM motors, both these attributes can be set to the same values. The value of this attribute comes from a Motor Tuning Data Source instance. | 532.1 H
|  | 2=Autotune Result | 152 | Pm Motor Lq Inductance | Status | Get | REAL | Indicates the phase-neutral, q-axis, inductance (in H) of a permanent magnet motor. For surface permanent magnet motors, the Lq and Ld inductances are the same or similar. For SPM motors, both these attributes can be set to the same values. The value of this attribute comes from a Motor Tuning Data Source instance. | —
|  | 3=Autotune Saved 4=User-specified | 152 | Pm Motor Lq Inductance | Configuration | Set(1) | REAL | Indicates the phase-neutral, q-axis, inductance (in H) of a permanent magnet motor. For surface permanent magnet motors, the Lq and Ld inductances are the same or similar. For SPM motors, both these attributes can be set to the same values. The value of this attribute comes from a Motor Tuning Data Source instance. | 0.0…6553.5 H(2)
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 153 | Pm Motor Lq Inductance State | Constant | Get | USINT | Indicates the state of the Permanent Magnet Motor Lq Inductance attribute (152) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set
|  | 2=Autotune Result | 153 | Pm Motor Lq Inductance State | Status | Get | USINT | Indicates the state of the Permanent Magnet Motor Lq Inductance attribute (152) value; that is, whether it is valid and how the value was determined. | —
|  | 3=Autotune Saved 4=User-specified | 153 | Pm Motor Lq Inductance State | Configuration | Set(1) | USINT | Indicates the state of the Permanent Magnet Motor Lq Inductance attribute (152) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set (default) 1=Invalid, Measurement Failed: An attempt was made to measure the value of the attribute, but it failed. 2=Valid, Calculated 3=Valid, User Supplied 4=Valid, Measured
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 154 | Pm Motor Ld Inductance | Constant | Get | REAL | Indicates the phase-neutral, d-axis, inductance (in H) of a permanent magnet motor. For surface permanent magnet motors, the Lq and Ld inductances are the same or similar. For SPM motors, both these attributes can be set to the same values. The value of this attribute comes from a Motor Tuning Data Source instance. | 179.1 H
|  | 2=Autotune Result | 154 | Pm Motor Ld Inductance | Status | Get | REAL | Indicates the phase-neutral, d-axis, inductance (in H) of a permanent magnet motor. For surface permanent magnet motors, the Lq and Ld inductances are the same or similar. For SPM motors, both these attributes can be set to the same values. The value of this attribute comes from a Motor Tuning Data Source instance. | —
|  | 3=Autotune Saved 4=User-specified | 154 | Pm Motor Ld Inductance | Configuration | Set(1) | REAL | Indicates the phase-neutral, d-axis, inductance (in H) of a permanent magnet motor. For surface permanent magnet motors, the Lq and Ld inductances are the same or similar. For SPM motors, both these attributes can be set to the same values. The value of this attribute comes from a Motor Tuning Data Source instance. | 0.0…6553.5 H(2)
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 155 | Pm Motor Ld Inductance State | Constant | Get | USINT | Indicates the state of the Permanent Magnet Motor Ld Inductance attribute (154) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set
|  | 2=Autotune Result | 155 | Pm Motor Ld Inductance State | Status | Get | USINT | Indicates the state of the Permanent Magnet Motor Ld Inductance attribute (154) value; that is, whether it is valid and how the value was determined. | —
|  | 3=Autotune Saved 4=User-specified | 155 | Pm Motor Ld Inductance State | Configuration | Set(1) | USINT | Indicates the state of the Permanent Magnet Motor Ld Inductance attribute (154) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set (default) 1=Invalid, Measurement Failed: An attempt was made to measure the value of the attribute, but it failed. 2=Valid, Calculated 3=Valid, User Supplied 4=Valid, Measured
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 156 | Pm Motor Rotary Voltage Constant | Constant | Get | REAL | Indicates the voltage, or back-EMF, constant of a rotary permanent magnet motor in volts (RMS) at the motor rated speed. It is assumed the back-EMF from the motor is sinusoidal. | 328.0V
|  | 2=Autotune Result | 156 | Pm Motor Rotary Voltage Constant | Status | Get | REAL | Indicates the voltage, or back-EMF, constant of a rotary permanent magnet motor in volts (RMS) at the motor rated speed. It is assumed the back-EMF from the motor is sinusoidal. | —
|  | 3=Autotune Saved 4=User-specified | 156 | Pm Motor Rotary Voltage Constant | Configuration | Set(1) | REAL | Indicates the voltage, or back-EMF, constant of a rotary permanent magnet motor in volts (RMS) at the motor rated speed. It is assumed the back-EMF from the motor is sinusoidal. | 0…1200.0V(2) Default=328.0V
0x0422 (1058) | Motor Tuning Data Source | 1=Default | 157 | Pm Motor Rotary Voltage Constant State | Constant | Get | USINT | Indicates the state of the Permanent Magnet Motor Rotary Voltage Constant attribute (156) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set
|  | 2=Autotune Result | 157 | Pm Motor Rotary Voltage Constant State | Status | Get | USINT | Indicates the state of the Permanent Magnet Motor Rotary Voltage Constant attribute (156) value; that is, whether it is valid and how the value was determined. | —
|  | 3=Autotune Saved 4=User-specified | 157 | Pm Motor Rotary Voltage Constant State | Configuration | Set(1) | USINT | Indicates the state of the Permanent Magnet Motor Rotary Voltage Constant attribute (156) value; that is, whether it is valid and how the value was determined. | 0=Invalid, Not Set (default) 1=Invalid, Measurement Failed: An attempt was made to measure the value of the attribute, but it failed. 2=Valid, Calculated 3=Valid, User Supplied 4=Valid, Measured
0x0432 (1074) | Motor Thermal Overload | 1=Motor 1 Overload | 1 | Thermal Capacity Utilized | Status | Get | REAL | Indicates the percentage of motor thermal capacity that the model has determined has been used. A value of 100% indicates that all thermal capacity has been used and the motor is likely hot enough to cause damage. | 0…100%
0x0432 (1074) | Motor Thermal Overload | 1=Motor 1 Overload | 2 | Current Above Overload | Status | Get | BOOL | Indicates whether the motor is being overloaded; that is, current to the motor exceeds Overload Current attribute (101). When the motor is in an overload state, the Thermal Capacity Utilized attribute (1) increases in value. The amount of increase depends on the magnitude of the current above the overload current setting. When the motor is not in an overload state, the Thermal Capacity Utilized attribute decreases in value, modeling motor cooling. | 0=Motor is not in an overload state. 1=Motor is in an overload state.
0x0432 (1074) | Motor Thermal Overload | 1=Motor 1 Overload | 3 | In Thermal Overload | Status | Get | BOOL | Indicates whether the Thermal Capacity Utilized is above 100%. | 0=Thermal Capacity Utilized is below 100%. 1=Thermal Capacity Utilized is above 100%.
0x0432 (1074) | Motor Thermal Overload | 1=Motor 1 Overload | 101 | Overload Current | Configuration | Set(1) | REAL | Sets the output current level above which the motor is assumed to be overloaded. When in an overload state, the Thermal Capacity Utilized attribute will increase in value. The amount of increase depends on the magnitude of the current above the overload current. When not in an overload state, the Thermal Capacity Utilized attribute will decrease in value, modeling motor cooling. | 0.0…12.0 A(2)
0x0432 (1074) | Motor Thermal Overload | 1=Motor 1 Overload | 102 | Thermal Model | Constant | Get | USINT | Indicates the thermal model used to calculate the Thermal Capacity Utilized. | 3=NEMA Trip Class 10
0x0432 (1074) | Motor Thermal Overload | 1=Motor 1 Overload | 106 | Derate Frequency | Configuration | Set(1) | REAL | Lets the thermal capacity be derated (reduced) when the frequency being output to the motor is below a specified value. When the frequency is below the derate frequency but the motor is in an overload condition, the Thermal Capacity Utilized attribute (1) increases at a rate higher than normal. This can be used to account for the fact that the cooling of most motors is reduced at low speeds. | 0.0…60.0 Hz
0x0432 (1074) | Motor Thermal Overload | 1=Motor 1 Overload | 107 | Power Up Behavior | Configuration | Set(1) | USINT | Defines the behavior of the motor thermal overload feature when the device powers up. | 0=Assume Motor Cold: The value of the Thermal Capacity Utilized attribute is reset to 0 on power up. This assumes the motor is completely cool. 1=Use Saved Thermal Capacity Utilized: The value of the Thermal Capacity Utilized attribute is saved at power down and restored on power up. This assumes the motor has not cooled at all while the product was off. 2=Model Motor Cooling During Power Down: The value of the Thermal Capacity Utilized attribute is saved at power down. The value is then reduced on power up to account for motor cooling while the unit was powered down, based on the amount of time the unit was powered down. (default)
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed 4=Frequency Closed Loop Velocity Regulator 5=Permanent Magnet Motor Current Regulator | 1 | Enable | Configuration | Set(1) | BOOL | Enables or disables the application of the specified adjustments. | 0=Disable 1=Enable (default)
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed 4=Frequency Closed Loop Velocity Regulator 5=Permanent Magnet Motor Current Regulator | 2 | Model Type | Constant | Get | USINT | Indicates the type of control model that is being adjusted. | 3= Proportional-integral (PI): The model combines proportional and integral elements.
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed 4=Frequency Closed Loop Velocity Regulator 5=Permanent Magnet Motor Current Regulator | 3 | Model Usage | Constant | Get | UINT | Indicates the usage or purpose of the control model being adjusted; that is, what it is trying to control or regulate. | 2=Velocity Regulator: The control model is being used to regulate a velocity value.
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed | 10 | Operational Limit, Minimum | Constant | Get | REAL | Indicates the value of the operational variable below which the model settings defined in this instance are not used and will not be operational. | 0
0x0447 (1095) |  | 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed | 10 | Operational Limit, Minimum | Status | Get | REAL | Indicates the value of the operational variable below which the model settings defined in this instance are not used and will not be operational. | —
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed | 11 | Operational Limit, Maximum | Configuration | Set(1) | REAL | Defines the value of the operational variable below which the model settings defined in this instance are not used and will not be operational. | Default values: For Vector Velocity Regulator, Low Speed instance (1)=4.998 For Vector Velocity Regulator, Mid Speed instance (2)=9.0 For Vector Velocity Regulator, High Speed (3)=12.0
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed 4=Frequency Closed Loop Velocity Regulator | 100 | Proportional Gain, Current | Status | Get | REAL | For models of type P, PI, and PID, this indicates the current value being used for the proportional gain in the control model. | —
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed 4=Frequency Closed Loop Velocity Regulator | 101 | Proportional Gain, Value Source | Configuration | Set(1) | USINT | For models of type P, PI, and PID, this attribute determines the source of the value in the Proportional Gain, Current attribute (100). | 0=Default: Current value is the Proportional Gain, Default attribute (102) value. (default) 1=User: Current value is the Proportional Gain, User attribute (103) value. 3=Calculated, from Bandwidth: Current value is a calculated value that uses the Bandwidth Target, Current attribute (130) value as an input.
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed 4=Frequency Closed Loop Velocity Regulator | 102 | Proportional Gain, Default | Constant | Get | REAL | For models of type P, PI, and PID, this indicates the default value used for the proportional gain in the control model. | For instances 1…3=100 rad/s For instance 4=5.0 rad/s
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed 4=Frequency Closed Loop Velocity Regulator | 103 | Proportional Gain, User | Configuration | Set | REAL | For models of type P, PI, and PID, this lets you define a value for manual adjustment of the proportional gain used in the control model. | 0.0…500.0 rad/s Default value: For instances 1…3=100.0 rad/s Varies for instance 4.
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed 4=Frequency Closed Loop Velocity Regulator | 110 | Integral Gain, Current | Status | Get | REAL | For models of type I, PI and PID, this is the current value (in rad/s) being used for the integral gain in the control model. | —
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed 4=Frequency Closed Loop Velocity Regulator | 111 | Integral Gain, Value Source | Configuration | Set(1) | USINT | For models of type I, PI, and PID, this attribute determines the source of the value in the attribute Integral Gain, Current attribute (110). | 0=Default: Current value is the Integral Gain, Default attribute (112) value. (default) 1=User: Current value is the Integral Gain, User attribute (113) value. 3=Calculated, from Bandwidth: Current value is a calculated value that uses the Bandwidth Target, Current attribute (130) value as an input.
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed 4=Frequency Closed Loop Velocity Regulator | 112 | Integral Gain, Default | Constant | Get | REAL | For models of type I, PI and PID, this is the default value used for the integral gain in the control model. | For instances 1…3=0.1 rad/s For instance 4=2.0 rad/s
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed 4=Frequency Closed Loop Velocity Regulator | 113 | Integral Gain, User | Configuration | Set(1) | REAL | For models of type P, PI, and PID, this lets you define a value for manual adjustment of the integral gain used in the control model. | 0.0…10.0 Default values: For instances 1…3=0.1 rad/s Varies for instance 4.
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed 5=Permanent Magnet Motor Current Regulator | 130 | Bandwidth Target, Current | Status | Get | REAL | Indicates the current target bandwidth (in rad/s)for the control model, which can be used to calculate or suggest values for other control model settings. | —
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed 5=Permanent Magnet Motor Current Regulator | 131 | Bandwidth Target, Source | Configuration | Set(1) | USINT | Defines the source of the value of the attribute Bandwidth Target, Current attribute (130). | 0=Default: Current value is the Bandwidth Target, Default attribute (132) value. (default) 1=User: Current value is the Bandwidth Target, User attribute (133) value. 3=Dynmic: Current value is a dynamic value that can change based on system conditions or configuration.
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed 5=Permanent Magnet Motor Current Regulator | 132 | Bandwidth Target, Default | Constant | Get | REAL | Indicates the default value for the control model bandwidth target, a fixed value chosen to provide good performance for common systems. | For instances 1…4=62.83 rad/s for instance 5=0.0 rad/s
0x0447 (1095) | Control Model Adjustment | 1=Vector Velocity Regulator, Low Speed 2=Vector Velocity Regulator, Mid Speed 3=Vector Velocity Regulator, High Speed 5=Permanent Magnet Motor Current Regulator | 133 | Bandwidth Target, User | Configuration | Set(1) | REAL | Defines a default value for the control model bandwidth target. | 0.0…251.33 Default values: For instances 1…3=62.83 rad/s Varies for instance 5.
-1 | Configuration attributes are settable through the user interface of the configuration software. If changes are made by using another method, the changed values may be overwritten when a connection is re-established or the device is power cycled.
-2 | The Attribute values listed are for the full range of Armor PowerFlex drives. The valid range for your catalog number is shown in the user interface of the Logix Designer application, where you configure your drive.

## Motor Control Objects
Armor PowerFlex CIP Object Definitions
For more information see:
Armor PowerFlex AC Drives User Manual, publication 35-UM001.
Class | Name | Instance | Attribute | Attribute Name | Data Classification | Access Rule | Data Type | Description | Attribute Values
0x041B | Motor Control Supervisor | 1 = Supervisor | 1 | Active Source | Status | Get | UINT | Indicates the number of the motor control source object (0x041C) instance that is actively controlling motor operation in the device. | 0=No source configured 1=Keypad 2=Assembly 3=Assembly Class 3 4=Safety Safe Stop
0x041B | Motor Control Supervisor | 1 = Supervisor | 100 | Run Commanded | Status | Get | BOOL | Indicates whether motion control is in a running state (normal or jog). | 0=Motion control stopped. 1=Motion control is running (normal or jog state).
0x041B (1051) | Motor Control Supervisor | 1 = Supervisor | 101 | Jog Commanded | Status | Get | BOOL | Indicates whether motion control is jogging. | 0=Motion control is stopped. 1=Motion control is running in jog mode.
0x041B (1051) | Motor Control Supervisor | 1 = Supervisor | 102 | Direction Commanded | Status | Get | USINT | Indicates the current commanded direction of motion when the Run Commanded attribute (100) is true (1). | 0=Reverse 1=Forward
0x041B (1051) | Motor Control Supervisor | 1 = Supervisor | 106 | Ready To Run | Status | Get | BOOL | Indicates whether motor control is ready to run. If this value is 0, any attempts to run or start motion control are rejected. For example, this value is set to 0 if the motor control source (0x041C) stop attribute (101) is set to true (1). | 0=Not ready to run. 1=Motor control ready to run.
0x041B (1051) | Motor Control Supervisor | 1 = Supervisor | 107 | Run Inhibits | Status | Get | ULINT | Provides additional information about the exactly which sources or conditions are preventing motor control from running. If any bits are set in this attribute, the Ready To Run attribute (106) is set to 0. | 0=Faulted: Device is in a faulted state. 1=Alarm: Device has an active alarm. 2=Stop: Device is receiving a stop signal from a source. 3=Precharge: Device is in the precharge state, with insufficient power for motion. 4=Safe Torque Off: Safety circuitry / safe torque off functionality is preventing motion. 5=Configuration Update: Device is in the middle of a configuration update. 6=Firmware Update: Device is performing a firmware update. 24=Power Section Not Powered: No AC power or disconnect switch is off. 25…31=Product Specific Inhibits
0x041B (1051) | Motor Control Supervisor | 1 = Supervisor | 108 | Last Run Inhibits | Status | Get | UDINT | Provides additional information about the exactly which sources / conditions prevented the device from entering the run mode when the last attempt was made. The value of the attribute Run Inhibits is latched into this attribute on every run attempt by the active source (whether successful or not). | 0=Faulted: Device is in a faulted state. 1=Alarm: Device has an active alarm. 2=Stop: Device is receiving a stop signal from a source. 3=Precharge: Device is in the precharge state, with insufficient power for motion. 4=Safe Torque Off: Safety circuitry / safe torque off functionality is preventing motion. 5=Configuration Update: Device is in the middle of a configuration update. 6=Firmware Update: Device is performing a firmware update. 24=Power Section Not Powered: No AC power or disconnect switch is off. 25…31=Product Specific Inhibits
0x041B (1051) | Motor Control Supervisor | 1 = Supervisor | 109 | Running | Status | Get | BOOL | Indicates whether motion control is running; that is, a start was commanded, motion control has been informed and is actively running. | 0=Motion control is not running. 1=Motion control is running.
0x041B (1051) | Motor Control Supervisor | 1 = Supervisor | 110 | Direction Running | Status | Get | USINT |  | 0=Reverse 1=Forward
0x041C (1051) | Motor Control Source | 1 = Keypad 2 = Assembly 3 = Assembly Class 3 | 1 | Enable | Configuration | Set(1) | BOOL | Lets the source be enabled or disabled. When enabled, the source can become operational. | 0=Source disabled 1=Source enabled (default)
|  | 4 = Safety Safe Stop | 1 | Enable | Constant | Get | BOOL | Indicates Whether the source is enabled and can become operational. | 1=Source enabled
0x041C (1051) | Motor Control Source | 1 = Keypad 2 = Assembly 3 = Assembly Class 3 | 2 | Inhibit | Control | Set | BOOL | Lets the source be inhibited and temporarily disabled (ignored). While inhibited, it cannot become the active control source. | 0=Source is not inhibited and can become the active source. (default) 1=Source is inhibited.
|  | 4 = Safety Safe Stop | 2 | Inhibit | Constant | Get | BOOL | Indicates whether the source is inhibited or not. | 0=Source is not inhibited and can become the active source.
0x041C (1051) | Motor Control Source | 1 = Keypad 2 = Assembly 3 = Assembly Class 3 4 = Safety Safe Stop | 3 | Operational | Status | Get | BOOL | Indicates whether the source instance is currently operational. | 0=Source is not operating and cannot become the active source. 1=Source is operating and can become the active source.
0x041C (1051) | Motor Control Source | 1 = Keypad 2 = Assembly 3 = Assembly Class 3 4 = Safety Safe Stop | 4 | Operational State | Status | Get | USINT | Indicates the operational state or operating condition of the source. | 0=OK: Source is operating normally. 1=Data Invalid: Source is operating, but one or more input data attributes are invalid and should not be used. 2=Faulted: Source has experienced a fault condition while operating. Logic related to the source may not be running or may be only partially active.
0x041C (1051) | Motor Control Source | 1 = Keypad 2 = Assembly 3 = Assembly Class 3 4 = Safety Safe Stop | 5 | Priority | Constant | Get | UINT | Indicates the order in which multiple operational sources are considered when a single active source needs to be determined. Higher values mean greater priority in the active source determination. If two values share the same priority value, priority is determined by instance number (lowest instance number has highest priority). | For Keypad instance (1)=50 For Assembly instance (2)=40 For AssemblyClass3 instance (3)=30 For SafetySafeStop instance (4)=55
0x041C (1051) | Motor Control Source | 2 = Assembly | 9 | Action Data Invalid | Configuration | Set(1) | USINT | Defines the action that the source should perform when the operational state changes from OK to Data Invalid. Lets you configure a proper response to conditions where no valid data is available. | 0=None: No action is taken, source remains operational. 1=Invalidate: Source is invalidated and is no longer operational; lower priority sources can become active. 2=Fault: A fault of type Data Invalid, Fault is declared. Source is invalidated. 4=Safe State: The data for the source is placed in a safe state, source remains operational. (default)
0x041C (1051) | Motor Control Source | 2 = Assembly 3 = Assembly Class 3 | 10 | Action Faulted | Configuration | Set(1) | USINT | Defines the action that the source should perform when the operational state changes from OK to Faulted. Lets you configure a proper response to conditions where the source is faulted. | 0=None: No action is taken, source remains operational. 1=Invalidate: Source is invalidated and is no longer operational, lower priority sources can become active. 2=Fault: A fault of type Source Faulted, Fault is declared. Source is invalidated. 4=Safe State: The data for the source is placed in a safe state, source remains operational. (default)
0x041C (1051) | Motor Control Source | 1 = Keypad 2 = Assembly 3 = Assembly Class 3 4 = Safety Safe Stop | 12 | Valid | Status | Get | BOOL | Indicates whether the source should be used as the active control source even if it is enabled and not inhibited. | 0=Source should not be used as the active control source even if it is enabled and not inhibited. 1=Source is valid and should be used.
0x041C (1051) | Motor Control Source | 1 = Keypad 2 = Assembly 3 = Assembly Class 3 4 = Safety Safe Stop | 100 | Start | Control | Set | BOOL | Start bit, for 3 wire control. Device enters normal run mode on a 0 to 1 momentary transition of this attribute. A transition of the Stop attribute (101) causes the device to stop running. | See Description.
0x041C (1051) | Motor Control Source | 1 = Keypad 2 = Assembly 3 = Assembly Class 3 4 = Safety Safe Stop | 101 | Stop | Control | Set | BOOL | Stop bit, for 3 wire control. Device exits run mode on a 0 to 1 momentary transition of this attribute. A transition of the Start attribute (100) causes the device to start running. | See Description.
0x041C (1051) | Motor Control Source | 1 = Keypad 2 = Assembly 3 = Assembly Class 3 4 = Safety Safe Stop | 102 | Run | Control | Set | BOOL | Run bit, for 2 wire control. Device enters normal run mode and stays there as long as this attribute remains 1. | See Description.
0x041C (1051) | Motor Control Source | 1 = Keypad 2 = Assembly 3 = Assembly Class 3 4 = Safety Safe Stop | 103 | Jog | Control | Set | BOOL | Jog bit, setting to 1 causes the device to run in jog mode as long as this attribute remains 1. | See Description.
0x041C (1051) | Motor Control Source | 1 = Keypad 2 = Assembly 3 = Assembly Class 3 4 = Safety Safe Stop | 104 | Direction | Control | Set | USINT | Commands the direction of motion when the drive is running. | 0=No Command 1=Forward Command (default) 2=Reverse Command
0x041E (1054) | Velocity Control Supervisor | 1=Supervisor | 1 | Active Source | Status | Get | UINT | Indicates the instance number of Velocity Control Source (0x041F) instance currently actively controlling velocity in the device. | 1=Preset 1 instance 2=Preset 2 instance 3=Preset 3 instance 4=Preset 4 instance 5=Jog instance 6=Assembly instance 7=Assembly Class 3 instance
0x041E (1054) | Velocity Control Supervisor | 1=Supervisor | 100 | Velocity Commanded Raw | Status | Get | REAL | Indicates the raw commanded velocity value from the active source. | —
0x041E (1054) | Velocity Control Supervisor | 1=Supervisor | 101 | Velocity Commanded | Status | Get | REAL | Indicates the commanded velocity based on the active source, velocity limits, and velocity skip bands. This commanded velocity is what is provided to the speed regulator motor control function. This commanded velocity may not equal the commanded velocity in the active control source due to the application of minimum and maximum velocity attributes, and velocity skip band | —
0x041E (1054) | Velocity Control Supervisor | 1=Supervisor | 104 | Current Velocity | Status | Get | REAL | Indicates the current velocity of the connected motor. Depending on the selected motor control mode and feedback device, the speed may be estimated. | —
0x041E (1054) | Velocity Control Supervisor | 1=Supervisor | 105 | At Commanded Velocity | Status | Get | BOOL | Indicates whether the motor is operating at the commanded velocity. | 0=The motor is not operating at the commanded velocity. 1=The motor is operating at the commanded velocity.
0x041E (1054) | Velocity Control Supervisor | 1=Supervisor | 201 | Maximum Forward Velocity | Configuration | Set(1) | REAL | Defines the maximum commanded velocity allowed in the forward direction. If a larger velocity is specified by a control source, velocity will be forced to this maximum value. | 0.0…400.0 revolutions/second Default=30.0
0x041E (1054) | Velocity Control Supervisor | 1=Supervisor | 203 | Minimum Forward Velocity | Configuration | Set(1) | REAL | Defines the minimum commanded velocity allowed in the forward direction. If a smaller velocity is specified by a control source, velocity will be forced to this minimum value. | 0.0…400.0 revolutions/second Default=0.0
0x041F (1055) | Velocity Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog | 1 | Enable | Constant | Get | BOOL | Indicates that the source is enabled and can become operational. | 1=Source Enabled
|  | 6=Assembly 7=Assembly Class 3 | 1 | Enable | Configuration | Set(1) | BOOL | Lets the source be enabled or disabled. When enabled, the source can become operational. | 0=Source Disabled (Default for Assembly Class3 instance 7) 1=Source Enabled (Default for Assembly instance 6)
0x041F (1055) | Velocity Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog | 2 | Inhibit | Constant | Get | BOOL | Indicates that the source is not inhibited. | 0=Source is not inhibited and can become the active source.
|  | 6=Assembly 7=Assembly Class 3 | 2 | Inhibit | Control | Set | BOOL | Lets the source be inhibited and temporarily disabled (ignored). While inhibited, it cannot become the active control source. | 0=Source is not inhibited and can become the active source. (Default for Assembly Class3 instance 7) 1=Source is inhibited.(Default for Assembly instance 6)
0x041F (1055) | Velocity Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog 6=Assembly 7=Assembly Class 3 | 3 | Operational | Status | Get | BOOL | Indicates whether the source instance is currently operational. | 0=Source is not operating and cannot become the active source. 1=Source is operating and can become the active source.
0x041F (1055) | Velocity Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog 6=Assembly 7=Assembly Class 3 | 4 | Operational State | Status | Get | USINT | Indicates the operational state or operating condition of the source. | 0=OK: Source is operating normally. 1=Data Invalid: Source is operating, but one or more input data attributes are invalid and should not be used. 2=Faulted: Source has experienced a fault condition while operating. Logic related to the source may not be running or may be only partially active.
0x041F (1055) | Velocity Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog 6=Assembly 7=Assembly Class 3 | 5 | Priority | Constant | Get | UINT | Indicates the order in which multiple operational sources are considered when a single active source needs to be determined. Higher values mean greater priority in the active source determination. If two values share the same priority value, priority is determined by instance number (lowest instance number has highest priority). | For Preset 1 instance (1)=50 For Preset 2 instance (2)=49 For Preset 3 instance (3)=48 For Preset 4 instance (4)=47 For Jog instance (5)=100 For Assembly instance (6)=90 For Assembly Class3 instance (7)=70
0x041F (1055) | Velocity Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog | 6 | Reference Ok | Constant | Get | UINT | Indicates the instance number of a source instance whose input values should be used instead of the ones in this instance when the operational state is OK. This attribute allows one control source to reference multiple other control sources. | 0
|  | 6=Assembly 7=Assembly Class 3 | 6 | Reference Ok | Control | Set | UINT | Defines the instance number of a source instance whose input values should be used instead of the ones in this instance when the operational state is OK. This attribute allows one control source to reference multiple other control sources. | 0…4 Default= 4
0x041F (1055) | Velocity Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 | 100 | Velocity | Status | Get | REAL | Indicates the velocity to be commanded by the Velocity Control Supervisor when this source is active. | —
|  | 5=Jog 6=Assembly 7=Assembly Class 3 | 100 | Velocity | Control | Set | REAL | Defines the velocity to be commanded by the Velocity Control Supervisor when this source is active. | Default= 0
0x041F (1055) | Velocity Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 | 101 | Velocity Path | Constant | Get | EPATH | Path (EPATH of structure USINT) to a CIP object attribute used to obtain the value of the Velocity attribute. If this attribute points to another attribute, the value of that attribute is copied to the Velocity attribute in this instance. This allows an indirect reference to the Velocity attribute value to be specified in certain special cases, like velocity presets. | 1=Velocity Preset 1 2=Velocity Preset 2 3=Velocity Preset 3 4=Velocity Preset 4 5= Jog Preset
0x0420 (1056) | Acceleration Control Supervisor | 1=Supervisor | 1 | Active Source | Status | Get | UINT | Indicates the instance number of Acceleration Control Source (0x041f) instance currently actively determining acceleration or deceleration behavior in the device. | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog 6=Assembly 7=Assembly Class 3 8=Dynamic
0x0420 (1056) | Acceleration Control Supervisor | 1=Supervisor | 100 | Acceleration Time Commanded | Status | Get | REAL | Indicates the acceleration (in seconds) time being commanded by the selected control source. | —
0x0420 (1056) | Acceleration Control Supervisor | 1=Supervisor | 101 | Deceleration Time Commanded | Status | Get | REAL | Indicates the deceleration (in seconds) time being commanded by the selected control source. | —
0x0420 (1056) | Acceleration Control Supervisor | 1=Supervisor | 102 | Acceleration Scurve Commanded | Status | Get | REAL | Sets the amount of acceleration or deceleration time applied to the ramp to soften the acceleration. This is also known as jerk reduction or ramp jerk control. A value of 0% results in no S-curve profile; that is, a linear acceleration ramp. A value of 100% results in a triangular S-curve profile, with the maximum acceleration occuring in the middle of the acceleration time. | 0-100%
0x0420 (1056) | Acceleration Control Supervisor | 1=Supervisor | 104 | Accelerating | Status | Get | BOOL | Indicates whether the motor is accelerating (velocity is increasing). | 0=Motor is not accelerating. 1=Motor is accelerating.
0x0420 (1056) | Acceleration Control Supervisor | 1=Supervisor | 105 | Decelerating | Status | Get | BOOL | Indicates whether the motor is decelerating (velocity is decreasing). | 0=Motor is not decelerating. 1=Motor is decelerating.
0x0421 (1057) | Acceleration Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog | 1 | Enable | Constant | Get | BOOL | Indicates that the source is enabled and can become operational. | 1=Source enabled.
|  | 6=Assembly 7=Assembly Class 3 8=Dynamic | 1 | Enable | Configuration | Set(1) | BOOL | Lets the source be enabled or disabled. When enabled, the source can become operational. | 0=Source Disabled (Default for Assembly Class3 instance 7) 1=Source Enabled (Default for Assembly instance 6)
0x0421 (1057) | Acceleration Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog | 2 | Inhibit | Constant | Get | BOOL | Indicates that the source is not inhibited. | 0=Source is not inhibited and can become the active source.
|  | 6=Assembly 7=Assembly Class 3 8=Dynamic | 2 | Inhibit | Control | Set | BOOL | Lets the source be inhibited and temporarily disabled (ignored). While inhibited, it cannot become the active control source. | 0=Source is not inhibited and can become the active source. (Default for Assembly Class3 instance 7) 1=Source is inhibited.(Default for Assembly instance 6)
0x0421 (1057) | Acceleration Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog 6=Assembly 7=Assembly Class 3 8=Dynamic | 3 | Operational | Status | Get | BOOL | Indicates whether the source instance is currently operational. | —
0x0421 (1057) | Acceleration Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog 6=Assembly 7=Assembly Class 3 8=Dynamic | 4 | Operational State | Status | Get | USINT | Indicates the operational state or operating condition of the source. | 0=OK: Source is operating normally. 1=Data Invalid: Source is operating, but one or more input data attributes are invalid and should not be used. 2=Faulted: Source has experienced a fault condition while operating. Logic related to the source may not be running or may be only partially active.
0x0421 (1057) | Acceleration Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog 6=Assembly 7=Assembly Class 3 8=Dynamic | 5 | Priority | Constant | Get | UINT | Indicates the order in which multiple operational sources are considered when a single active source needs to be determined. Higher values mean greater priority in the active source determination. If two values share the same priority value, priority is determined by instance number (lowest instance number has highest priority). | For Preset 1 instance (1)=50 For Preset 2 instance (2)=49 For Preset 3 instance (3)=48 For Preset 4 instance (4)=47 For Jog instance (5)=100 For Assembly instance (6)=90 For Assembly Class3 instance (7)=70
0x0421 (1057) | Acceleration Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog | 6 | Reference Ok | Constant | Get | UINT | Indicates the instance number of a source instance whose input values should be used instead of the ones in this instance when the operational state is OK. This attribute allows one control source to reference multiple other control sources. | 0
|  | 6=Assembly 7=Assembly Class 3 8=Dynamic | 6 | Reference Ok | Control | Set | UINT | Defines the instance number of a source instance whose input values should be used instead of the ones in this instance when the operational state is OK. This attribute allows one control source to reference multiple other control sources. | 0…4 Default= 4
0x0421 (1057) | Acceleration Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 | 100 | Acceleration Time | Status | Get | REAL | Indicates the acceleration time (in seconds) to be commanded by the Acceleration Control Supervisor. | —
|  | 5=Jog 6=Assembly 7=Assembly Class 3 8=Dynamic | 100 | Acceleration Time | Control | Set | REAL | Defines the acceleration time (in seconds) to be commanded by the Acceleration Control Supervisor. | —
0x0421 (1057) | Acceleration Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 | 101 | Deceleration Time | Status | Get | REAL | Indicates the deceleration time (in seconds) to be commanded by the Acceleration Control Supervisor. | —
|  | 5=Jog 6=Assembly 7=Assembly Class 3 8=Dynamic | 101 | Deceleration Time | Control | Set | REAL | Defines the deceleration time (in seconds) to be commanded by the Acceleration Control Supervisor. | —
0x0421 (1057) | Acceleration Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 | 102 | Acceleration Scurve | Status | Get | REAL | Indicates the Acceleration S-Curve and Deceleration S-curve percentage to be commanded by the Acceleration Control Supervisor. | —
|  | 5=Jog 6=Assembly 7=Assembly Class 3 8=Dynamic | 102 | Acceleration Scurve | Control | Set | REAL | Defines the Acceleration S-Curve and Deceleration S-curve percentage to be commanded by the Acceleration Control Supervisor. | —
0x0421 (1057) | Acceleration Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog | 1000 | Acceleration Time Path | Constant | Get | EPATH | Path (EPATH) to a CIP object attribute used to obtain the value of the Acceleration Time attribute. If this attribute points to another attribute, the value of that attribute is copied to the Acceleration Time attribute in this instance. This allows an indirect reference to the Acceleration Time attribute value to be specified in certain special cases like acceleration presets. | 1=Acceleration Preset 1 2=Acceleration Preset 2 3=Acceleration Preset 3 4=Acceleration Preset 4 5=Jog Preset
0x0421 (1057) | Acceleration Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog | 1001 | Deceleration Time Path | Constant | Get | EPATH | Path (EPATH) to a CIP object attribute used to obtain the value of the Deceleration Time attribute. If this attribute points to another attribute, the value of that attribute is copied to the Deceleration Time attribute in this instance. This allows an indirect reference to the Acceleration Time attribute value to be specified in certain special cases like acceleration presets. | 1=Acceleration Preset 1 2=Acceleration Preset 2 3=Acceleration Preset 3 4=Acceleration Preset 4 5=Jog Preset
0x0421 (1057) | Acceleration Control Source | 1=Preset 1 2=Preset 2 3=Preset 3 4=Preset 4 5=Jog | 1002 | Acceleration Scurve Path | Constant | Get | EPATH | Path (EPATH) to a CIP object attribute used to obtain the value of the Acceleration S-Curve attribute. If this attribute points to another attribute, the value of that attribute is copied to the Acceleration S-Curve attribute in this instance. This allows an indirect reference to the Acceleration Time attribute value to be specified in certain special cases like acceleration presets. | 1=Acceleration Preset 1 2=Acceleration Preset 2 3=Acceleration Preset 3 4=Acceleration Preset 4 5=Jog Preset
0x0429 (1065) | Stop Control Supervisor | 1=Supervisor | 1 | Active Source | Status | Get | UINT | Indicates the number of the Stop Control Source instance currently actively determining the stop settings in the device. If set to 0, the coast stop mode will be used. | 0=Instance not defined. Use coast stop mode. 1=Default instance 2=Fault instance 3=Safety STO instance 4=SafetySS1 instance 5=Safety SS2 instance
0x0429 (1065) | Stop Control Supervisor | 1=Supervisor | 101 | Stop Mode | Status | Get | USINT | Indicates the stop mode being commanded for the current stop, or the stop mode that will be used for the next stop. | 1=Coast: Power to the motor is immediately removed. 2=Ramp: Velocity is reduced to zero at a rate determined by the Deceleration Time attribute (101) of the Acceleration Control Source object (040421). Power to the motor is removed when velocity is zero. (default) 4=DC Brake: Power to the motor is not interrupted, but a user-defined amount of DC current is injected into the motor to produce a more rapid stop.
0x0429 (1065) | Stop Control Supervisor | 1=Supervisor | 102 | Stopping | Status | Get | BOOL | Indicates whether the device is in a stopping mode and performing the stop action. | 0=Not in stopping mode. 1=A stop command was accepted and the device is performing the stop action.
0x0429 (1065) | Stop Control Supervisor | 1=Supervisor | 103 | DC Brake Level | Status | Get | REAL | Indicates the the amount of current injected into the motor during a DC Brake stop. | 0.0…10.8A(2)
0x0429 (1065) | Stop Control Supervisor | 1=Supervisor | 104 | DC Brake Time | Status | Get | REAL | Indicates the length of time that DC brake current is injected into the motor when the Stop Mode (101) is DC Brake. If DC Brake Automatic Off (105) is set to true (1), this represents a maximum time not a fixed duration. | 0.0…99.9 seconds
0x0429 (1065) | Stop Control Supervisor | 1=Supervisor | 105 | DC Brake Automatic Off | Status | Get | BOOL | Indicates whether the DC Brake Automatic Off feature is enabled and DC Brake operation will be automatically stopped when zero speed is reached. | 0=DC Brake Automatic Off is disabled. 1=DC Brake Automatic Off is enabled.
0x0429 (1065) | Stop Control Supervisor | 1=Supervisor | 106 | DC Braking | Status | Get | BOOL | Indicates whether DC braking injection is currently being performed. DC braking can be active outside of a stop when it is used as part of another funtion, such as Flying Start. | 0=DC braking injection is not being performed. 1=DC braking injection is being performed.
0x0429 (1065) | Stop Control Supervisor | 1=Supervisor | 107 | Flux Brake Enabled | Status | Get | BOOL | Indicates whether flux braking is enabled for use during Ramp stop mode. Only applies to certain motor types, such as AC induction motors. | 0=Flux braking is disabled. 1=Flux braking is enabled.
0x0429 (1065) | Stop Control Supervisor | 1=Supervisor | 108 | Flux Braking | Status | Get | BOOL | Indicates whether flux braking is currently being performed during the current stop. This attribute is false (0) when the device is not performing a stop. | 0=Flux braking is not being performed. 1=Flux braking is being performed.
0x042A (1066) | Stop Control Source | 1=Default 2=Fault 3=Safety STO 4=SafetySS1 | 1 | Enable | Constant | Get | BOOL | Indicates whether the source is enabled and can become operational. | 1=Source Enabled
0x042A (1066) | Stop Control Source | 1=Default 2=Fault 3=Safety STO 4=SafetySS1 | 2 | Inhibit | Constant | Get | BOOL | Indicates whether the source is inhibited or not. | 0=Source is not inhibited and can become the active source.
0x042A (1066) | Stop Control Source | 1=Default 2=Fault 3=Safety STO 4=SafetySS1 | 3 | Operational | Status | Get | BOOL | Indicates whether the source instance is currently operational. | 0=Source is not operating and cannot become the active source. 1=Source is operating and can become the active source.
0x042A (1066) | Stop Control Source | 1=Default 2=Fault 3=Safety STO 4=SafetySS1 | 4 | Operational State | Status | Get | USINT | Indicates the operational state or operating condition of the source. | 0=OK: Source is operating normally. 1=Data Invalid: Source is operating, but one or more input data attributes are invalid and should not be used. 2=Faulted: Source has experienced a fault condition while operating. Logic related to the source may not be running or may be only partially active.
0x042A (1066) | Stop Control Source | 1=Default 2=Fault 3=Safety STO 4=SafetySS1 | 5 | Priority | Constant | Get | UINT | Indicates the order in which multiple operational sources are considered when a single active source needs to be determined. Higher values mean greater priority in the active source determination. If two values share the same priority value, priority is determined by instance number (lowest instance number has highest priority). | For Default instance (1)=90 For Fault instance (2)=100 For SafetySTO instance (3)=95 For SafetySS1 instance (4)=95
0x042A (1066) | Stop Control Source | 1=Default 3=Safety STO 4=SafetySS1 | 100 | Stop Mode | Configuration | Set(1) | USINT | Defines which stop mode to use when a stop command is received. | 1=Coast: Power to the motor is immediately removed. 2=Ramp: Velocity is reduced to zero at a rate determined by the Deceleration Time attribute (101) of the Acceleration Control Source object (040421). Power to the motor is removed when velocity is zero. 4=DC Brake: Power to the motor is not interrupted, but a user-defined amount of DC current is injected into the motor to produce a more rapid stop.
|  | 2=Fault | 100 | Stop Mode | Status | Get | USINT | Defines which stop mode to use when a stop command is received. | 1=Coast: Power to the motor is immediately removed. 2=Ramp: Velocity is reduced to zero at a rate determined by the Deceleration Time attribute (101) of the Acceleration Control Source object (040421). Power to the motor is removed when velocity is zero. 4=DC Brake: Power to the motor is not interrupted, but a user-defined amount of DC current is injected into the motor to produce a more rapid stop.
0x042A (1066) | Stop Control Source | 1=Default 3=Safety STO 4=SafetySS1 | 101 | Dc Brake Level | Configuration | Set(1) | REAL | Defines the amount of current injected into the motor during a DC Brake stop. | See the section in the user manual on how to configure stop control.
|  | 2=Fault | 101 | Dc Brake Level | Status | Get | REAL | Indicates the amount of current injected into the motor during a DC Brake stop. | See the section in the user manual on how to configure stop control.
0x042A (1066) | Stop Control Source | 1=Default 3=Safety STO 4=SafetySS1 | 102 | Dc Brake Time | Configuration | Set(1) | REAL | Defines the length of time that DC brake current is injected into the motor when the stop mode is "DC Brake". | 0.0…99.9 seconds (default=0)
|  | 2=Fault | 102 | Dc Brake Time | Status | Get | REAL | Indicates the length of time that DC brake current is injected into the motor when the stop mode is "DC Brake".
0x042A (1066) | Stop Control Source | 1=Default 3=Safety STO 4=SafetySS1 | 103 | Dc Brake Automatic Off | Configuration | Set(1) | BOOL | Enables or disables DC Brake Automatic Off feature which stops DC Brake operation when zero speed is reached instead of performing DC braking for the configured DC Brake Time (102). | 0=DC Brake operation is performed for the configured DC Brake Time (attribute 102). (default) 1=DC Brake operation is automatically stopped when zero speed is reached.
|  | 2=Fault | 103 | Dc Brake Automatic Off | Status | Get | BOOL | Enables or disables DC Brake Automatic Off feature which stops DC Brake operation when zero speed is reached instead of performing DC braking for the configured DC Brake Time (102). | 0=DC Brake operation is performed for the configured DC Brake Time (attribute 102). (default) 1=DC Brake operation is automatically stopped when zero speed is reached.
0x042A (1066) | Stop Control Source | 1=Default 3=Safety STO 4=SafetySS1 | 104 | Flux Brake Enabled | Configuration | Set(1) | BOOL | Defines whether flux braking should be applied during Ramp stop mode. Only applies to certain motor types, such as AC induction motors. | 0=Flux braking should not be applied. (default) 1=Flux braking may be applied.
|  | 2=Fault | 104 | Flux Brake Enabled | Status | Get | BOOL | Defines whether flux braking should be applied during Ramp stop mode. Only applies to certain motor types, such as AC induction motors. | 0=Flux braking should not be applied. (default) 1=Flux braking may be applied.
0x042C (1068) | Motor Control Configuration | 1=Motor Control Configuration | 1 | Control Mode | Configuration | Set(1) | USINT | Indicates the motor control mode; that is, which parameters the motor control in the device is controlling. | 2=Velocity Control: Device is controlling the velocity (speed) of the motor.
0x042C (1068) | Motor Control Configuration | 1=Motor Control Configuration | 2 | Control Method | Configuration | Set(1) | USINT | Indicates the motor control method; that is, the means by which the motor control in the device is controlling the motor. | 1=Frequency Control: Motor control is performed by varying the voltage magnitude and frequency output to the motor. 2=Vector Control: Motor control is performed by varying the voltage magnitude, angle between voltage and current, and frequency output to the motor. (default)
0x042C (1068) | Motor Control Configuration | 1=Motor Control Configuration | 4 | Motor Control Supervisor Instance | Status | Get | UINT | Indicates the instance number of the CIP Motor Control Supervisor object instance that is controlling the basic state of the motor. | 1=Motor Control Supervisor instance is active.
0x042C (1068) | Motor Control Configuration | 1=Motor Control Configuration | 5 | Velocity Control Supervisor Instance | Status | Get | UINT | Indicates the instance number of the CIP Velocity Control Supervisor object instance that is controlling the velocity of the motor. | 1=Velocity Control Supervisor instance is active.
0x042C (1068) | Motor Control Configuration | 1=Motor Control Configuration | 6 | Acceleration Control Supervisor Instance | Status | Get | UINT | Indicates the instance number of the CIP Acceleration Control Supervisor object instance that is controlling the acceleration of the motor. | 1=Acceleration Control Supervisor instance is active.
0x042C (1068) | Motor Control Configuration | 1=Motor Control Configuration | 9 | Stop Control Supervisor Instance | Status | Get | UINT | Indicates the instance number of the CIP Stop Control Supervisor object instance that is controlling the position of the motor. | 1=Stop Control Supervisor instance is active.
0x042C (1068) | Motor Control Configuration | 1=Motor Control Configuration | 10 | Motor Configuration Instance | Status | Get | UINT | Indicates the instance number of the CIP Advanced Motor Control Supervisor object instance that is controlling the position of the motor. | 1=Advanced Motor Configuration instance is active.
0x042D (1069) | Motor Control Method Frequency | 1=Motor Control Method Frequency | 1 | Volts Per Hertz Curve | Configuration | Set(1) | USINT | Defines the type of curve that is being applied to map frequency to output voltage. Select from fixed curve types or a custom (user-defined) curve that lets you set optional attributes to alter the curve for your application. | 0=Custom: A custom or user-defined curve can be specified by setting the optional attributes of the instance. 1=Variable Torque: Selects a curve suitable for variable torque loads such as fans and pumps. This type of curve has no starting or acceleration boost. 2=Constant Torque: Selects a curve suitable for constant torque loads such as conveyors and compressors. This type of curve has starting or acceleration boost, but no break voltage or frequency.
0x042D (1069) | Motor Control Method Frequency | 1=Motor Control Method Frequency | 3 | Start / Acceleration Boost Voltage | Configuration | Set(1) | REAL | Defines the boost voltage, which moves the voltage to frequency curve up, when starting or accelerating. The boost voltage is only applied until the specified break voltage/frequency point on the curve is reached. | 0.0…115.0V
0x042D (1069) | Motor Control Method Frequency | 1=Motor Control Method Frequency | 4 | Break Voltage | Configuration | Set(1) | REAL | Defines the voltage that the drive will output at the frequency specified by the Break Frequency attribute (5). | 0.0…460.0V
0x042D (1069) | Motor Control Method Frequency | 1=Motor Control Method Frequency | 5 | Break Frequency | Configuration | Set(1) | REAL | Defines the frequency at which the voltage specified by the Break Voltage attribute (4) is output. | 0.0…500.0 Hz Default = 15 Hz
0x042E (1070) | Motor Control Method Vector | 1=Motor Control Method Vector | 1 | Control Method Subtype | Configuration | Set(1) | USINT | Defines the type of vector control being used in the device. | 0=Sensorless Vector: The device is controlling the motor using current feedback, assuming that the total current is the vector sum of the torque- and flux-producing components. (default) 1=Flux Vector: The device is controlling the motor using current feedback, with independent control of the torque- and flux-producing currents.
0x042E (1070) | Motor Control Method Vector | 1=Motor Control Method Vector | 2 | Svc Economizer Enable | Configuration | Set(1) | BOOL | Enables the use of economizer feature when the Control Method is Sensorless Vector. When a constant velocity is achieved, the economizer becomes active and automatically adjusts the drive output voltage based on the applied load. By matching the output voltage to the applied load, motor efficiency is optimized. | 0=The economizer feature is disabled. (default) 1=The economizer feature is enabled.
0x043D (1085) | Velocity Preset | 1=Velocity Preset 1 2=Velocity Preset 2 3=Velocity Preset 3 4=Velocity Preset 4 | 1 | Velocity | Configuration | Set(1) | REAL | Defines the velocity preset value. This attribute is typically linked to a Velocity attribute in a Velocity Control Source object (0x041f) instance using the Velocity Path (attribute 101) indirect input value mechanism. | 0.0…400.0 revolutions per second
0x043E (1086) | Acceleration Preset | 1=Acceleration Preset 1 2=Acceleration Preset 2 3=Acceleration Preset 3 4=Acceleration Preset 4 | 1 | Acceleration Time | Configuration | Set(1) | REAL | Defines the acceleration time preset value. This attribute is typically linked to an Acceleration Time attribute in an Acceleration Control Source object (0x0421) instance using the Acceleration Time Path (attribute 1000) indirect input value mechanism. | 0…600.0 seconds Default=10.0 seconds
0x043E (1086) | Acceleration Preset | 1=Acceleration Preset 1 2=Acceleration Preset 2 3=Acceleration Preset 3 4=Acceleration Preset 4 | 2 | Deceleration Time | Configuration | Set(1) | REAL | Defines the deceleration time preset value. This attribute is typically linked to a Deceleration Time attribute in an Acceleration Control Source object (0x0421)instance using the Deceleration Time Path (attribute 1001) indirect input value mechanism. | 0…600.0 seconds Default=10.0 seconds
0x043E (1086) | Acceleration Preset | 1=Acceleration Preset 1 2=Acceleration Preset 2 3=Acceleration Preset 3 4=Acceleration Preset 4 | 3 | Acceleration Scurve | Configuration | Set(1) | REAL | Defines the acceleration s-curve preset value. This attribute is typically linked to an Acceleration S-Curve attribute in an Acceleration Control Source object (0x0421)instance using the Acceleration S-Curve Path (attribute 1002) indirect input value mechanism. | 0.0…100.0% Default=0.0%
0x043F (1087) | Discrete Output Control Source | 1=Out 0: I/O Assembly 2=Out 0: Class 3 Assembly 3=Out 0: AC Power 4=Out 0: Fault 5=Out 1: I/O Assembly 6=Out 1: Class 3 Assembly 7=Out 1: AC Power 8=Out 1: Fault | 1 | Enable | Configuration | Set(1) | BOOL | Lets the source be enabled or disabled. When enabled, the source can become operational. | 0=Source disabled 1=Source enabled
0x043F (1087) | Discrete Output Control Source | 1=Out 0: I/O Assembly 2=Out 0: Class 3 Assembly 3=Out 0: AC Power 4=Out 0: Fault 5=Out 1: I/O Assembly 6=Out 1: Class 3 Assembly 7=Out 1: AC Power 8=Out 1: Fault | 2 | Inhibit | Control | Set | BOOL | Lets the source be inhibited and temporarily disabled (ignored). While inhibited, it cannot become the active control source. | 0=Source is not inhibited and can become the active source. 1=Source is inhibited. (default)
0x043F (1087) | Discrete Output Control Source | 1=Out 0: I/O Assembly 2=Out 0: Class 3 Assembly 3=Out 0: AC Power 4=Out 0: Fault 5=Out 1: I/O Assembly 6=Out 1: Class 3 Assembly 7=Out 1: AC Power 8=Out 1: Fault | 3 | Operational | Status | Get | BOOL | Indicates whether the source instance is currently operational. | 0=Source is not operating and cannot become the active source. 1=Source is operating and can become the active source.
0x043F (1087) | Discrete Output Control Source | 1=Out 0: I/O Assembly 2=Out 0: Class 3 Assembly 5=Out 1: I/O Assembly 6=Out 1: Class 3 Assembly 7=Out 1: AC Power | 4 | Operational State | Status | Get | USINT | Indicates the operational state or operating condition of the source. | 0=OK: Source is operating normally. 1=Data Invalid: Source is operating, but one or more input data attributes are invalid and should not be used. 2=Faulted: Source has experienced a fault condition while operating. Logic related to the source may not be running or may be only partially active.
|  | 3=Out 0: AC Power 4=Out 0: Fault 7=Out 1: AC Power 8=Out 1: Fault | 4 | Operational State | Constant | Get | USINT | Indicates the operational state or operating condition of the source. | 0=OK: Source is operating normally.
0x043F (1087) | Discrete Output Control Source | 1=Out 0: I/O Assembly 2=Out 0: Class 3 Assembly 3=Out 0: AC Power 4=Out 0: Fault 5=Out 1: I/O Assembly 6=Out 1: Class 3 Assembly 7=Out 1: AC Power 8=Out 1: Fault | 5 | Priority | Constant | Get | UINT | Indicates the order in which multiple operational sources are considered when a single active source needs to be determined. Higher values mean greater priority in the active source determination. If two values share the same priority value, priority is determined by instance number (lowest instance number has highest priority). | For Fault instances (4) and (8) = 60 For AC Power instances (3) and (7) = 50 For I/O Assembly instances (1) and (5) = 40 For Class 3 Assembly instances (2) and (6) = 30
0x043F (1087) | Discrete Output Control Source | 1=Out 0: I/O Assembly 5=Out 1: I/O Assembly | 9 | Action, Data Invalid | Configuration | Set(1) | USINT | Defines the action that the source should perform when the operational state changes from OK to Data Invalid. Lets you configure a proper response to conditions where no valid data is available. Not used for instance Out 0: Class 3 Assembly (2), instance Out 0: AC Power (3), instance Out 0: Fault (4), instance Out 1: Class 3 Assembly (6), instance Out 1: AC Power (7), and instance Out 1: Fault (8) | 0=None: No action is taken; the source remains operational. Because there is no valid data for the source, the existing object data is held (hold last state). 1=Invalidate: Source is invalidated and is no longer operational. Lower priority sources can become active. 2=Fault: A Data Invalid, Fault is declared. Source is invalidated. 3=Alarm: A Data Invalid, Alarm is declared. Source is invalidated. 4=Safe State: The data for the source is placed in a safe state and the source remains operational. (default) 5=On State: The data for the source is placed in a "on" state. The source remains operational. 6=Off State: The data for the source is placed in a "off" state. The source remains operational.
0x043F (1087) | Discrete Output Control Source | 1=Out 0: I/O Assembly 2=Out 0: Class 3 Assembly 5=Out 1: I/O Assembly 6=Out 1: Class 3 Assembly | 10 | Action, Faulted | Configuration | Set(1) | USINT | Defines the action that the source should perform when the operational state changes from OK to Faulted. Lets you configure a proper response to conditions where the source is faulted. Not used for instance Out 0: AC Power (3), instance Out 0: Fault (4), instance Out 1: AC Power (7), and instance Out 1: Fault (8) | 0=None: No action is taken; the source remains operational. Because there is no valid data for the source, the existing object data is held (hold last state). 1=Invalidate: Source is invalidated and is no longer operational. Lower priority sources can become active. 2=Fault: A Data Invalid, Fault is declared. Source is invalidated. 3=Alarm: A Data Invalid, Alarm is declared. Source is invalidated. 4=Safe State: The data for the source is placed in a safe state and the source remains operational. (default) 5=On State: The data for the source is placed in a "on" state. The source remains operational. 6=Off State: The data for the source is placed in a "off" state. The source remains operational.
0x043F | Discrete Output Control Source | 2=Out 0: Class 3 Assembly 3=Out 0: AC Power 4=Out 0: Fault 6=Out 1: Class 3 Assembly 7=Out 1: AC Power 8=Out 1: Fault | 11 | Action, Ok | Configuration | Set(1) | USINT | Defines the action that the source should perform when the operational state changes to OK from any other state, and when the Operational attribute (3) changes from false (0) to true (1) while the operational state is OK. Lets you configure if and how the data associated with the source is updated when it becomes operational in the normal or OK state. Not used for instance Out 0: I/O Assembly (1), and instance Out 1: I/O Assembly (5). | 0=None: No action is taken. (default) 1=Hold State: Source data is populated with the current output data from the supervisor. Thus if this source becomes the active source, there will be no change in the supervisor output data if no data is available for the source. 2=Safe State: Source data is populated with defined safe state values. This confirms that the supervisor output data is in a defined safe state if no data is available for the newly operational source. 3=On State: Source data is populated with defined on state values. This lets the newly operational source put the supervisor output in an on state even if no data is available for the source. 4=Off State: Source data is populated with defined off state values. This lets the newly operational source put the supervisor output in an off state even if no data is available for the source.
0x043F (1087) | Discrete Output Control Source | 1=Out 0: I/O Assembly 2=Out 0: Class 3 Assembly 3=Out 0: AC Power 4=Out 0: Fault 5=Out 1: I/O Assembly 6=Out 1: Class 3 Assembly 7=Out 1: AC Power 8=Out 1: Fault | 12 | Valid | Status | Get | BOOL | Indicates whether the source should be used as the active control source even if it is enabled and not inhibited. | 0=Source should not be used as the active control source even if it is enabled and not inhibited. 1=Source is valid and should be used.
0x043F (1087) | Discrete Output Control Source | 1=Out 0: I/O Assembly 2=Out 0: Class 3 Assembly 3=Out 0: AC Power 4=Out 0: Fault 5=Out 1: I/O Assembly 6=Out 1: Class 3 Assembly 7=Out 1: AC Power 8=Out 1: Fault | 13 | Supervisor Instance | Constant | Get | UINT | Indicates the number of the supervisor object (Discrete Output Poing object 0x0009)that uses this source. | For Out0 instances (1), (2), (3), (4)=1 For Out1 instances (5), (6), (7), (8)=2
0x043F (1087) | Discrete Output Control Source | 1=Out 0: I/O Assembly 2=Out 0: Class 3 Assembly 3=Out 0: AC Power 4=Out 0: Fault 5=Out 1: I/O Assembly 6=Out 1: Class 3 Assembly 7=Out 1: AC Power 8=Out 1: Fault | 100 | Value | Control | Set | BOOL | Defines the discrete output value to be used by the Discrete Output Point object (0x0009). | 0=Output point should be off. (default) 1=Output point should be on.
0x0446 (1094) | Jog Preset | 1=JogPreset | 1 | Velocity | Configuration | Set(1) | REAL | Defines the velocity preset value for jogging. This attribute is typically linked to a Velocity attribute in a Velocity Control Source object (0x041f) instance using the Velocity Path (attribute 101) indirect input value mechanism. | 0.0…400.0 revolutions per second
0x0446 (1094) | Jog Preset | 1=JogPreset | 2 | Acceleration Time | Configuration | Set(1) | REAL | Defines the acceleration time preset value for jogging. This attribute is typically linked to an Acceleration Time attribute in an Acceleration Control Source object (0x0421) instance using the Acceleration Time Path (attribute 1000) indirect input value mechanism. | 0…600.0 seconds Default=10.0 seconds
0x0446 (1094) | Jog Preset | 1=JogPreset | 3 | Deceleration Time | Configuration | Set(1) | REAL | Defines the deceleration time preset value for jogging. This attribute is typically linked to a Deceleration Time attribute in an Acceleration Control Source object (0x0421)instance using the Deceleration Time Path (attribute 1001) indirect input value mechanism. | 0…600.0 seconds Default=10.0 seconds
0x0446 (1094) | Jog Preset | 1=JogPreset | 4 | Acceleration Scurve | Configuration | Set(1) | REAL | Defines the acceleration or deceleration s-curve preset value for jogging. This attribute is typically linked to an Acceleration S-Curve attribute in an Acceleration Control Source object (0x0421)instance using the Acceleration S-Curve Path (attribute 1002) indirect input value mechanism. | 0.0…100.0% Default=0.0%
0x0446 (1094) | Jog Preset | 1=JogPreset | 6 | Direction | Configuration | Set(1) | USINT | Defines the direction of motion while jogging. | 0=No Command: Direction during jog is not defined. Direction will be determined by another control source. (default) 1=Forward Command: Direction during jog is forward only. This cannot be overridden. 2=Reverse Command: Direction during jog is reverse only. This cannot be overridden.
-1 | Configuration attributes are settable through the user interface of the configuration software. If changes are made by using another method, the changed values may be overwritten when a connection is re-established or the device is power cycled.
-2 | The Attribute values listed are for the full range of Armor PowerFlex drives. The valid range for your catalog number is shown in the user interface of the Logix Designer application, where you configure your drive.

## Physical Objects
Armor PowerFlex CIP Object Definitions
For more information see:
Armor PowerFlex AC Drives User Manual, publication 35-UM001.
Class | Name | Instance | Attribute | Attribute Name | Data Classification | Access Rule | Data Type | Description | Attribute Values
0x0423 (1059) | Temperature Sensor | 1=System Board Temperature 2=Power Board Temperature 3=VFD IGBT Temperature 4=System Processor Temperature | 1 | Current Temperature | Status | Get | REAL | Indicates the current temperature, in °C, being measured by the temperature sensor. | —
0x0423 (1059) | Temperature Sensor | 1=System Board Temperature 2=Power Board Temperature 3=VFD IGBT Temperature 4=System Processor Temperature | 2 | Valid | Status | Get | BOOL | Indicates whether the temperature value being reported by the Current Temperature attribute is valid. This attribute can be used to indicate situations where an optional temperature sensor is not installed, or there is a hardware problem with a temperature sensor | 0=Temperature value is not valid. 1=Temperature is valid.
0x0423 (1059) | Temperature Sensor | 1=System Board Temperature 2=Power Board Temperature 3=VFD IGBT Temperature 4=System Processor Temperature | 7 | High Limit Hard | Constant | Get | REAL | Indicates the fixed or hard upper limit on the temperature being measured, above which an "Overtemperature, Hard" condition is declared. | For System Board Temperature Instance (1)=85°C For Power Board Temperature Instance (2)=105°C For VFD IGBT Board Temperature Instance (3)=125°C For System Processor Temperature Instance (4)=90°C
0x0426 (1062) | Power Supply | 1=External Unswitched 24V Power Supply 2=External Switched 24V Power Supply 3=Internal 24V Power Supply 4=Three-phase AC Power (for motor) | 1 | Type | Constant | Get | UDINT | Indicates the type of power supply that the object represents. For informational purposes only. | For instances 1 and 2=0:External DC For instance 3=1:Internal DC For instance 4=2:External AC
0x0426 (1062) | Power Supply | 1=External Unswitched 24V Power Supply 2=External Switched 24V Power Supply 3=Internal 24V Power Supply 4=Three-phase AC Power (for motor) | 2 | Measured Voltage | Status | Get | REAL | Indicates the current power supply voltage being measured. The reported value may have some filtering applied so that this value may not reflect an instantaneous voltage. | —
0x0426 (1062) | Power Supply | 1=External Unswitched 24V Power Supply 2=External Switched 24V Power Supply 3=Internal 24V Power Supply 4=Three-phase AC Power (for motor) | 4 | Within Voltage Limits | Status | Get | BOOL | Indicates whether the Measured Voltage (attribute 2) is currently within the specified hard and/or soft voltage limits. | 0=Measured voltage is outside of the specified limits 1=Measured voltage is within the specific limits
0x0426 (1062) | Power Supply | 1=External Unswitched 24V Power Supply 2=External Switched 24V Power Supply 3=Internal 24V Power Supply 4=Three-phase AC Power (for motor) | 6 | Active | Status | Get | BOOL | For internal power supplies, this attribute indicates whether the power supply is on; that is, it is producing a non-zero voltage. For external power supplies, this attribute indicates that power is being applied from an outside source. | 0=Power supply is not active. 1=Power supply is active.
0x0426 (1062) | Power Supply | 1=External Unswitched 24V Power Supply 2=External Switched 24V Power Supply 3=Internal 24V Power Supply 4=Three-phase AC Power (for motor) | 7 | Switchable | Constant | Get | BOOL | Indicates whether the power supply is switchable. This means that the power supply has a mechanism whereby the power being supplied to the end device can be interrupted via a physical switch or other virtual means. | For instances 1…3=0:Power supply is not switchable. For instance 4=1:Power supply is switchable.
0x0426 (1062) | Power Supply | 4=Three-phase AC Power (for motor) | 8 | Physical Switch State | Status | Get | BOOL | Indicates the state of the switch for power supplies that are switchable via a physical switch. | 0=The physical switch is in the off position. Power is not being supplied to the end device. 1=The physical switch is in the on position. Power is being supplied to the end device.
0x0426 (1062) | Power Supply | 1=External Unswitched 24V Power Supply 2=External Switched 24V Power Supply 3=Internal 24V Power Supply 4=Three-phase AC Power (for motor) | 100 | Nominal Voltage | Constant | Get | REAL | Indicates nominal or expected voltage of the power supply. | For instances 1…3=24.0V For instance 4=480.0V
0x0426 (1062) | Power Supply | 1=External Unswitched 24V Power Supply 2=External Switched 24V Power Supply 3=Internal 24V Power Supply | 101 | Voltage Low Limit Hard | Constant | Get | REAL | Indicates the fixed or hard lower limit on the voltage of the power supply, below which an "undervoltage, hard" condition is declared. | 20.4V
0x0426 (1062) | Power Supply | 1=External Unswitched 24V Power Supply 2=External Switched 24V Power Supply 3=Internal 24V Power Supply | 102 | Voltage High Limit Hard | Constant | Get | REAL | Indicates the fixed or hard upper limit on the voltage of the power supply, above which an "overvoltage, hard" condition is declared. | 26.4V
0x0438 | Drive Power Loss Supervisor | 1=Supervisor | 100 | Power Loss Present | Status | Get | BOOL | Indicates whether the device is in a power loss state based on the conditions being monitored by an active power loss source. | 0=The device is not in a power loss state. 1=The device is in a power loss state.
0x0439 (1081) | Drive Power Loss Source | 1 = Power Supply Three Phase AC | 100 | Power Loss Present | Status | Get | BOOL | Indicates whether the power loss source is detecting a power loss condition. | 0=Power loss not detected. 1=Power loss detected.
0x0439 (1081) | Drive Power Loss Source | 1 = Power Supply Three Phase AC | 102 | Immediate Action | Configuration | Set(1) | USINT | Defines an action to take immediately when a power loss condition is detected. | 0=Stop: Disables output from the device, causing the attached motor to coast. (default) 1=Continue: Continue normal operation. Do not take any special action. 2=Decelerate: Reduce output frequency from an inverter, which causes attached motor to declerate.
0x0439 (1081) | Drive Power Loss Source | 1 = Power Supply Three Phase AC | 103 | Trigger Voltage | Configuration | Set(1) | REAL | Defines the voltage level below which the device is considered to be in a power loss condition; that is, the level at which a power loss is triggered. | 430V (default) or 280V
0x0440 (1088) | Fan | 1=Heatsink Fan | 1 | Type | Constant | Get | UDINT | Indicates the type of fan that the object represents. For informational purposes only. | 1=Internal or Integrated Axial
0x0440 (1088) | Fan | 1=Heatsink Fan | 2 | Actual State | Status | Get | BOOL | Indicates the actual state of the fan: on or off. | 0=Fan is off. 1=Fan is on.
0x0440 (1088) | Fan | 1=Heatsink Fan | 3 | Commanded State | Status | Get | BOOL | Commands the fan to turn on or off. | 0=Commanded state is off. 1=Commanded state is on.
0x0440 (1088) | Fan | 1=Heatsink Fan | 4 | Measured Speed | Status | Get | REAL | Indicates the actual speed of the fan, in revolutions per minute, determined by measurement. The reported value may have some filtering applied so that this value may not reflect an instantaneous speed. | —
0x0440 (1088) | Fan | 1=Heatsink Fan | 5 | Commanded Speed | Status | Get | REAL | Commands the fan to rotate at a specific speed (in revolutions per minute). | —
0x0440 (1088) | Fan | 1=Heatsink Fan | 6 | Within Speed Limits | Status | Get | BOOL | Indicates whether the Measured Speed (attribute 4) is currently within the specified hard and/or soft speed limits. | 0=Measured Speed (attribute 4) is outside of the specified limits (attributes 7 and 8). 1=Measured Speed (attribute 4) is within the specified limits (attributes 7 and 8).
0x0440 (1088) | Fan | 1=Heatsink Fan | 7 | Speed Low Limit Hard | Constant | Get | REAL | Indicates the fixed or hard lower limit on the speed of the fan, in revolutions per minute, below which an "underspeed, hard" condition is declared. | 2600.00 rpm
0x0440 (1088) | Fan | 1=Heatsink Fan | 8 | Speed High Limit Hard | Constant | Get | REAL | Indicates the fixed or hard upper limit on the speed of the fan, in revolutions per minute, above which an "overspeed, hard" condition is declared. | 3800.0 rpm
-1 | Configuration attributes are settable through the user interface of the configuration software. If changes are made by using another method, the changed values may be overwritten when a connection is re-established or the device is power cycled.

## Predictive Maintenance Objects
Armor PowerFlex CIP Object Definitions
For more information see:
Armor PowerFlex AC Drives User Manual, publication 35-UM001.
Class | Name | Instance | Attribute | Attribute Name | Data Classification | Access Rule | Data Type | Description | Attribute Values
0x0414 (1044) | Predictive Maintenance Component | 1=VFD IGBTs 2=VFD DC Bus Capacitors 3=VFD Heatsink Fan 4=Disconnect Switch 5=Electromechanical Brake Contactor 6=Motor Lubrication 7=Machine Lubrication 8=Motor Bearing 9=Machine Bearing 10=User Maintenance | 1 | Component Type | Constant | Get | UINT | Specifies the type of physical component this instance represents. The type of physical component determines the type of predictive maintenance algorithm used to calculate component life. Additionally, components of the same type are often grouped together using the Predictive Maintenance Component Group object (0x0415). | IGBT Component Group Instance (1)=769:Power Device Group, IGBT Bus Capacitor Component Group Instance (2)=513=Capacitor Group, Bus Heatsink Fan Component Group Instance (3)=257=Fan Group, Heatsink Switch Component Group Instance (4)=1027=Switching Device Group, Switch Contactor Component Group Instance (5)=1025=Switching Device Group, Contactor Motor Lubrication Component Group Instance (6)=1537=Lubrication Group, Motor Machine Lubrication Component Group Instance (7)=1538=Lubrication Group, Machine Motor Bearing Component Group Instance (8)=1281=Bearing Group, Motor Machine Bearing Component Group Instance (9)=1282=Bearing Group, Machine Undefined Component Group Instance (10)=0:Group, Heterogenous. Used for groups that have components of a variety of types, which may include unknown types.
0x0414 (1044) | Predictive Maintenance Component | 1=VFD IGBTs 2=VFD DC Bus Capacitors 3=VFD Heatsink Fan 4=Disconnect Switch 5=Electromechanical Brake Contactor 6=Motor Lubrication 7=Machine Lubrication 8=Motor Bearing 9=Machine Bearing 10=User Maintenance | 2 | Remaining Life | Accumulator | Get | DINT | Displays the remaining hours of expected life for the component. | —
0x0414 (1044) | Predictive Maintenance Component | 1=VFD IGBTs 2=VFD DC Bus Capacitors 3=VFD Heatsink Fan 4=Disconnect Switch 5=Electromechanical Brake Contactor 6=Motor Lubrication 7=Machine Lubrication 8=Motor Bearing 9=Machine Bearing 10=User Maintenance | 3 | Remaining Life Units | Constant | Get | UINT | Indicates the units used to define the Remaining Life of the component. Hours are the preferred units, but counts may be more appropriate for simple components. For example Counts could indicate the number of cycles between operating and non-operating states. | 4356=Time/Hour
0x0414 (1044) | Predictive Maintenance Component | 1=VFD IGBTs 2=VFD DC Bus Capacitors 3=VFD Heatsink Fan 4=Disconnect Switch 5=Electromechanical Brake Contactor 6=Motor Lubrication 7=Machine Lubrication 8=Motor Bearing 9=Machine Bearing 10=User Maintenance | 4 | Elapsed Life | Accumulator | Get | UDINT | Displays the accumultated life, in hours or counts, that the component has been in operation. | —
0x0414 (1044) | Predictive Maintenance Component | 1=VFD IGBTs 2=VFD DC Bus Capacitors 3=VFD Heatsink Fan 6=Motor Lubrication 7=Machine Lubrication 8=Motor Bearing 9=Machine Bearing 10=User Maintenance | 5 | Elapsed Life Units | Constant | Get | UINT | Indicates the units used to define the accumulated life of the component in hours. | 4356=Time/Hour
|  | 4=Disconnect Switch 5=Electromechanical Brake Contactor | 5 | Elapsed Life Units | Constant | Get | UINT | Indicates the units used to define the accumulated life of the component. Counts could indicate the number of cycles between operating and non-operating states. | 4097=General/Count
0x0414 (1044) | Predictive Maintenance Component | 1=VFD IGBTs 2=VFD DC Bus Capacitors 3=VFD Heatsink Fan 4=Disconnect Switch 5=Electromechanical Brake Contactor 6=Motor Lubrication 7=Machine Lubrication 8=Motor Bearing 9=Machine Bearing 10=User Maintenance | 6 | Consumed Life Percentage | Accumulator | Get | REAL | Displays the consumed life of the component as a percentage of its total life. A value of 0% indicates a component has never been in operation. A value of 100% indicates the component has been in operation for its expected total life. Values greater than 100% are possible and indicate that the component has exceeded its expected total life. | —
0x0414 (1044) | Predictive Maintenance Component | 1=VFD IGBTs 2=VFD DC Bus Capacitors 3=VFD Heatsink Fan 4=Disconnect Switch 5=Electromechanical Brake Contactor 6=Motor Lubrication 7=Machine Lubrication 8=Motor Bearing 9=Machine Bearing 10=User Maintenance | 7 | Remaining Life Below Threshold | Status | Get | BOOL | Indicates whether the remaining life of the component has fallen below a user configured threshold level. The threshold level is configured in the Predictive Maintenance Component Group object (0x0415). The Remaining Life Threshold attribute from the group instance along with the Remaining Life attribute from this instance determine the state of this flag. | —
0x0414 (1044) | Predictive Maintenance Component | 1=VFD IGBTs 2=VFD DC Bus Capacitors 3=VFD Heatsink Fan 4=Disconnect Switch 5=Electromechanical Brake Contactor 6=Motor Lubrication 7=Machine Lubrication 8=Motor Bearing 9=Machine Bearing 10=User Maintenance | 8 | Operating | Status | Get | BOOL | Indicates whether the associated physical component is operating or is in its operational state. | 0=Not operating or not in operational state 1=Operating or in operational state. The component's remaining life is decreasing at a rate based on the predictive maintenance algorithm/model.
0x0414 (1044) | Predictive Maintenance Component | 3=VFD Heatsink Fan 6=Motor Lubrication 7=Machine Lubrication 8=Motor Bearing 9=Machine Bearing 10=User Maintenance | 9 | Reset Count | Accumulator | Get | UDINT | Indicates the number of times the component has had its predictive maintenance data reset via the Reset service. | —
0x0415 (1045) | Predictive Maintenance Component Group | 1=IGBT Component Group 2=Bus Capacitor Component Group 3=Heatsink Fan Component Group 4=Switch Component Group 5=Contactor Component Group 6=Motor Lubrication Component Group 7=Machine Lubrication Component Group 8=Motor Bearing Component Group 9=Machine Bearing Component Group 10=Undefined Component Group | 1 | Component Group Type | Constant | Get | UINT | Indicates the type of components in the component group. | IGBT Component Group Instance (1)=769:Power Device Group, IGBT Bus Capacitor Component Group Instance (2)=513=Capacitor Group, Bus Heatsink Fan Component Group Instance (3)=257=Fan Group, Heatsink Switch Component Group Instance (4)=1027=Switching Device Group, Switch Contactor Component Group Instance (5)=1025=Switching Device Group, Contactor Motor Lubrication Component Group Instance (6)=1537=Lubrication Group, Motor Machine Lubrication Component Group Instance (7)=1538=Lubrication Group, Machine Motor Bearing Component Group Instance (8)=1281=Bearing Group, Motor Machine Bearing Component Group Instance (9)=1282=Bearing Group, Machine Undefined Component Group Instance (10)=0:Group, Heterogenous. Used for groups that have components of a variety of types, which may include unknown types.
0x0415 (1045) | Predictive Maintenance Component Group | 1=IGBT Component Group 2=Bus Capacitor Component Group 3=Heatsink Fan Component Group 4=Switch Component Group 5=Contactor Component Group 6=Motor Lubrication Component Group 7=Machine Lubrication Component Group 8=Motor Bearing Component Group 9=Machine Bearing Component Group 10=Undefined Component Group | 2 | Number Of Components | Constant | Get | USINT | Displays the remaining hours of expected life for the component. | 1
0x0415 (1045) | Predictive Maintenance Component Group | 1=IGBT Component Group 2=Bus Capacitor Component Group 3=Heatsink Fan Component Group 4=Switch Component Group 5=Contactor Component Group 6=Motor Lubrication Component Group 7=Machine Lubrication Component Group 8=Motor Bearing Component Group 9=Machine Bearing Component Group 10=Undefined Component Group | 3 | Component Instance List | Constant | Get | Array of UINT | Lists the component (Predictive Maintenance Component object) instances represented by this component group instance. | —
0x0415 (1045) | Predictive Maintenance Component Group | 1=IGBT Component Group 2=Bus Capacitor Component Group 3=Heatsink Fan Component Group 4=Switch Component Group 5=Contactor Component Group | 4 | Enabled | Constant | Get | BOOL | Indicates that the component group is enabled. | 1=Enabled
|  | 6=Motor Lubrication Component Group 7=Machine Lubrication Component Group 8=Motor Bearing Component Group 9=Machine Bearing Component Group 10=Undefined Component Group | 4 | Enabled | Configuration | Set(1) | BOOL | Indicates whether the component group is enabled or disabled. | 0=Group is disabled. 1=Group is enabled. (default)
0x0415 (1045) | Predictive Maintenance Component Group | 1=IGBT Component Group 2=Bus Capacitor Component Group 3=Heatsink Fan Component Group 4=Switch Component Group 5=Contactor Component Group 6=Motor Lubrication Component Group 7=Machine Lubrication Component Group 8=Motor Bearing Component Group 9=Machine Bearing Component Group 10=Undefined Component Group | 5 | Remaining Life Threshold | Configuration | Set(1) | UDINT | Specifies a remaining life level below which components in this group take action to report a predictive maintenance event. The units applied to this attribute are determined though the Remaining Life Threshold Units attribute (7). | —
0x0415 (1045) | Predictive Maintenance Component Group | 1=IGBT Component Group 2=Bus Capacitor Component Group 3=Heatsink Fan Component Group 4=Switch Component Group 5=Contactor Component Group 6=Motor Lubrication Component Group 7=Machine Lubrication Component Group 8=Motor Bearing Component Group 9=Machine Bearing Component Group 10=Undefined Component Group | 6 | Remaining Life Threshold Action | Configuration | Set(1) | USINT | Specifies the action that components in this group should take when their remaining life falls below the configured threshold. | 0=Ignore (default) 1=Alarm
0x0415 (1045) | Predictive Maintenance Component Group | 1=IGBT Component Group 2=Bus Capacitor Component Group 3=Heatsink Fan Component Group 4=Switch Component Group 5=Contactor Component Group 6=Motor Lubrication Component Group 7=Machine Lubrication Component Group 8=Motor Bearing Component Group 9=Machine Bearing Component Group 10=Undefined Component Group | 7 | Remaining Life Threshold Units | Constant | Get | UINT | Indicates the engineering units being used for the Remaining Life Threshold attribute. | 4356=Time/Hour
0x0415 (1045) | Predictive Maintenance Component Group | 6=Motor Lubrication Component Group 7=Machine Lubrication Component Group 8=Motor Bearing Component Group 9=Machine Bearing Component Group 10=Undefined Component Group | 8 | User Maintenance Maximum Life | Configuration | Set(1) | UDINT | Lets you define the total life for all components in the group. This attribute allows the lifetime of components external to the product to be specified. | —
0x0415 (1045) | Predictive Maintenance Component Group | 1=IGBT Component Group 2=Bus Capacitor Component Group 3=Heatsink Fan Component Group 4=Switch Component Group 5=Contactor Component Group 6=Motor Lubrication Component Group 7=Machine Lubrication Component Group 8=Motor Bearing Component Group 9=Machine Bearing Component Group 10=Undefined Component Group | 9 | User Maintenance Maximum Life Units | Constant | Get | UINT | Indicates the engineering units being used for the User Maintenance Total Life attribute | 4356=Time/Hour
-1 | Configuration attributes are settable through the user interface of the configuration software. If changes are made by using another method, the changed values may be overwritten when a connection is re-established or the device is power cycled.

## Safety Objects
Armor PowerFlex CIP Object Definitions
For more information see:
Armor PowerFlex AC Drives User Manual, publication 35-UM001.
Class | Name | Instance | Attribute | Attribute Name | Data Classification | Access Rule | Data Type | Description | Attribute Values
0x0039 (57) | Safety Supervisor | 1=Safety Supervisor | 11 | Device Status | Status | Get | USINT | Indicates the current status of the device | 1=Self-Testing 2=Idle 3=Self-Test Exception 4=Executing 5=Abort 6=Critical Fault 7=Configuring 8=Waiting for TUNID 51=Waiting for TUNID with Torque Permitted 52=Executing with Torque Permitted
0x003B (59) | Safety Discrete Output Point | 1 and 2=Configuration for control by the Safety Output Assembly 3 and 4=Configuration for control by the SBC function | 3 | Safety Output Value | Status | Get | BOOL | Indicates the value that the output is commanded to be in. This is safety data. This value is settable only by safety I/O connection. | 0=Off 1=On The safe state of this safety data is 0.
0x003B (59) | Safety Discrete Output Point | 1 and 2=Configuration for control by the Safety Output Assembly 3 and 4=Configuration for control by the SBC function | 4 | Output Monitor Value | Status | Get | BOOL | Indicates the output point value. This is the relay state red back from the internal auxiliary contacts. This is not safety data. | 0=Off 1=On
0x003B (59) | Safety Discrete Output Point | 1 and 2=Configuration for control by the Safety Output Assembly 3 and 4=Configuration for control by the SBC function | 5 | Safety Status | Status | Get | BOOL | Indicates the safety output point status. This is safety data. | 0=Alarm 1=OK The safe state of this safety data is 0.
0x003B (59) | Safety Discrete Output Point | 1 and 2=Configuration for control by the Safety Output Assembly | 6 | Output Channel Mode | Configuration | Set (1) | USINT | Selects the output channel mode. | 0 = Not Used (default) 1 = Used, No Test Pulses 2 = Used, Test Pulses
|  | 3 and 4=Configuration for control by the SBC function | 6 | Output Channel Mode | Status | Get | USINT | Indicates the output channel mode. | 0 = Not Used (default) 1 = Used, No Test Pulses 2 = Used, Test Pulses
0x003B (59) | Safety Discrete Output Point | 1 and 2=Configuration for control by the Safety Output Assembly 3 and 4=Configuration for control by the SBC function | 100 | Output Ready | Status | Get | BOOL | Indicates that the Safety Discrete Output Point object is supported, configured, and is ready for operation. | 0=Ready 1=Not Ready
0x003B (59) | Safety Discrete Output Point | 6 and 2=Configuration for control by the Safety Output Assembly 3 and 4=Configuration for control by the SBC function | 110 | Alarm Type | Status | Get | USINT | Describes detailed information about the Alarm. Values 5 and 8 can occur when the corresponding input port is configured as Dual Channel. | 0=No alarm (Status=OK) 1=Invalid Configuration 2= Over-current detected 3= Short-circuit to low was detected (Read back signal error during an expected high state.) 4= Stuck-at-high detected (Test signal cannot be read back.) 5= Failure of the associated dual channel output 8= Dual Channel violation 9=Cross Connection detected
0x003D (61) | Safety Discrete Input Point | 1 – Safety Input 0 2 – Safety Input 1 3 – Safety Input 2 4 – Safety Input 3 | 3 | Input Port Value | Status | Get | BOOL | Indicates the input point value at the terminal prior to the on/off delay evaluation. This is not safety data. | 0=Off 1=On
0x003D (61) | Safety Discrete Input Point | 1 – Safety Input 0 2 – Safety Input 1 3 – Safety Input 2 4 – Safety Input 3 | 4 | Safety Status | Status | Get | BOOL | Contains the input point status value. This is safety data. | 0=Alarm 1=OK The safe state of this safety data is 0.
0x003D (61) | Safety Discrete Input Point | 1 – Safety Input 0 2 – Safety Input 1 3 – Safety Input 2 4 – Safety Input 3 | 5 | Off_On Delay | Configuration | Set (1) | UINT | Sets the filter time for off to on transition | 0…65535 ms Default=0 ms
0x003D (61) | Safety Discrete Input Point | 1 – Safety Input 0 2 – Safety Input 1 3 – Safety Input 2 4 – Safety Input 3 | 6 | On_Off Delay | Configuration | Set (1) | UINT | Sets the filter time for off to on transition | 0…65535 ms Default=0 ms
0x003D (61) | Safety Discrete Input Point | 1 – Safety Input 0 2 – Safety Input 1 3 – Safety Input 2 4 – Safety Input 3 | 7 | Safety Input Logical Value | Status | Get | BOOL | Contains the input point value after safety and on/off delay evaluation. This is safety data. | 0=Off 1=On The safe state of this safety data is 0.
0x003D (61) | Safety Discrete Input Point | 1 – Safety Input 0 2 – Safety Input 1 3 – Safety Input 2 4 – Safety Input 3 | 8 | Input Channel Mode | Configuration | Set (1) | USINT | Configures the input point mode. | 0=not used (default) 1=input, with test pulse from test out 2=input, no dependency to test out. (Used as semiconductor input). 3=input, no dependency to test out (Used as standard input).
0x003D (61) | Safety Discrete Input Point | 1 – Safety Input 0 2 – Safety Input 1 3 – Safety Input 2 4 – Safety Input 3 | 10 | Standard Input Value | Status | Get | BOOL | Indicates the input point value at the terminal with the on/off delay evaluation, but prior to safety input evaluation. This is not safety data. | 0=Off 1=On
0x003D (61) | Safety Discrete Input Point | 1 – Safety Input 0 2 – Safety Input 1 3 – Safety Input 2 4 – Safety Input 3 | 100 | Input Valid | Status | Get | BOOL | Safety Discrete Input Point object is supported, configured, and is producing valid data. | 0=Data Invalid 1=Data Valid
0x003D (61) | Safety Discrete Input Point | 1 – Safety Input 0 2 – Safety Input 1 3 – Safety Input 2 4 – Safety Input 3 | 110 | Alarm Type | Status | Get | USINT | Describes detailed information about the Alarm This attribute indicates whether the fault is a configuration error, external connection error, internal circuit error, discrepancy error, or fault on the associated SDIP point if configured for dual channel mode. Values 4 and 5 can occur when the corresponding input port is configured as “Used as Dual Channel”. | 0= No alarm (Status=OK) 1= Configuration error 2= External connected device error 3= Internal circuit error 4= Discrepancy error 5= Failure of the associated dual channel input
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 1 | Velocity Data Type | Constant | Get | USINT | Indicates the data type of Feedback velocity and Feedback Acceleration and all related attributes. | 1=REAL
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 2 | Feedback Position | Status | Get | DINT | Indicates the actual position of the feedback device. This is safety data. | Feedback Counts For rotary encoders: 1 (Rev)=(Feedback Resolution × Feedback Interpolation) Counts For linear encoders: 1 (Meter)=(Feedback Resolution × Feedback Interpolation) Counts The safe state is defined by Position Safe State Behavior attribute (11).
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 3 | Feedback Velocity | Status | Get | REAL | Indicates the Feedback velocity, the actual velocity of the feedback device. This is safety data. | The safe state is defined by Velocity Safe State Behavior attribute (13).
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 4 | Feedback Acceleration | Status | Get | REAL | Indicates the actual acceleration of the feedback device. This is safety data. | Magnitude: The calculated acceleration of the feedback device in feedback units per second squared. Sign: Defined as positive for increasing speed and negative for decreasing speed in either direction. The safe state is 0.
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 5 | Feedback Mode | Configuration | Set (1) | USINT | Defines the Motion Feedback Mode. | 0=Not Used (default) 1=Used
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 8 | Feedback Fault | Status | Get | BOOL | Status of this motion feedback channel. | 0=No Fault 1=Faulted
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 9 | Feedback Fault Reason | Status | Get | USINT | Determines cause of the fault that was detected. | 1=No Fault 2=Invalid Configuration 3=Exceeded Max Speed 4=Exceeded Max Acceleration 5=Sin²+Cos² Error 6=Quadrature Error 9=Supply Voltage Error 11=Feedback Signal Loss 107=Max Input Frequency 108=Sin/Cos Offset
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 10 | Reset Feedback Fault | Control | Set | BOOL | Resets a motion feedback fault with a 0 to 1 transition. | 0 to 1=Reset
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 11 | Position Safe State Behavior | Constant | Get | USINT | Defines behavior for value reporting when faulted. Specifies the value that the Safety Feedback should report in the feedback values to the safety controller whenever the feedback is in the Safe State. | 2=Hold Last Value
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 12 | Position Safe State Value | Constant | Get | DINT | Defines the Safe Position Feedback value that is reported in Position Feedback to the safety controller whenever Feedback Fault is Faulted and Position Safe State Behavior is Use Position Safe State Value. | 0
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 13 | Velocity Safe State Behavior | Constant | Get | USINT | Defines behavior for value reporting when faulted. Specifies the value that the Safety Feedback should report in the feedback values to the safety controller whenever the feedback is in the Safe State. | 0=Velocity Safe State Value
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 14 | Velocity Safe State Value | Constant | Get | REAL | Defines the Safe Velocity Feedback and Acceleration Feedback value that is reported in Velocity Feedback to the safety controller whenever Feedback Status is Faulted and Velocity Safe State Behavior is Use Velocity Safe State Value. | 0
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 16 | Feedback Unit | Configuration | Set (1) | USINT | Defines the Unit of measure for the feedback device. | 0=Rev (rotary devices)(default) 1=Meter (linear devices)
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 17 | Feedback Type | Configuration | Set (1) | USINT | Defines the type of feedback device. | 0=Not specified 1=Digital AqB 2=Sine/Cosine 3=Hiperface SC
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 18 | Feedback Polarity | Configuration | Set (1) | USINT | Defines the direction of counting versus direction of motion. Normal means counts increase when motion is in the positive direction. Inverted means that counts decrease when motion is in the positive direction. | 0=Normal (default) 1=Inverted
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 19 | Feedback Cycle Resolution | Configuration | Set (1) | UDINT | Defines the number of Cycles per Unit. The unit is typically meters for linear devices and revolutions for rotary devices.
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 20 | Feedback Cycle Interpolation | Configuration | Set (1) | UDINT | Defines the number of position Counts per Cycle.
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 22 | Velocity Average Time | Configuration | Set (1) | UINT | Specifies the time period over which to average Feedback Velocity. | 0=Disable Averaging (default) 1…65535 ms
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 23 | Acceleration Average Time | Configuration | Set (1) | UINT | Specifies the time period over which to average Feedback Acceleration. | 0=Disable Averaging (default) 1…65535 ms
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 24 | Feedback Voltage Monitor | Configuration | Set (1) | USINT | Selects monitoring of voltage supplied to power the feedback. | 0=Not Monitored (default) 1=4.75V to 5.25V 3=11.4V to 12.6V
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 26 | Feedback Maximum Speed | Configuration | Set (1) | REAL | Defines the maximum allowable speed. Exceeding this speed causes a fault. | Default = 0.0 Feedback Units / s, which means there is no maximum speed.
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 27 | Feedback Maximum Acceleration | Configuration | Set (1) | REAL | Defines the maximum allowable acceleration. Exceeding this acceleration causes a fault. | Default = 0.0 Feedback Units / s², which means there is no maximum speed.
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 29 | Feedback Position Long | Configuration | Set (1) | LINT | Defines the actual position of the feedback device. For rotary encoders: 1 (Rev) = (Feedback Resolution × Feedback Interpolation) Counts For linear encoders: 1 (Meter) = (Feedback Resolution × Feedback Interpolation) Counts | Feedback Counts The safe state is defined by Position Safe State Behavior attribute 11.
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 31 | Motion Positive | Status | Get | BOOL | Indicates positive motion. set to 1 when Feedback Velocity is greater than Standstill Speed. | 0=No Positive Motion 1=Positive Motion
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 32 | Motion Negative | Status | Get | BOOL | Indicates negative motion. Set to 1 when Feedback Velocity is less than -1 × Standstill Speed. | 0=No Negative Motion 1=Negative Motion
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 33 | Standstill Speed | Configuration | Set (1) | REAL | Defines the speed below which motion is considered stopped. Feedback Velocity above standstill speed will set either Motion Negative or Motion Positive attributes to 1. | Default = 0.0 Feedback Units / s
0x0058 (88) | Safety Feedback Object | 1=Interface to Encoder input | 110 | Feedback Valid | Status | Get | BOOL | Indicates whether the Safety Feedback object is supported, configured, not faulted, and is currently producing valid safety feedback data from a connected feedback device. | 0=Feedback Invalid 1=Feedback Valid
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 10 | Safety Reset | Control | Set | BOOL | Resets all safety functions on a transition from 0 to 1 after the cause of the fault is corrected. | 0→1=Reset
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 11 | Restart Type | Configuration | Set (1) | USINT | Defines safety function restart behavior while operating. If the Restart Type is Manual, a 0 to 1 transition of the Safety Reset attribute is required to restart a Safety Stop function. If the Restart Type is Automatic and there are no faults present, the Safety Stop function restarts when the safety function tag transitions from 0 to 1. | 0=Manual (default) 1=Automatic
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 12 | Cold Start Type | Configuration | Set (1) | USINT | Defines safety function restart behavior when applying controller power or mode change to Run. | 0=Manual (default) 1=Automatic
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 20 | Safety Feedback Instance | Configuration | Set (1) | UINT | Defines the instance ID of a Safety Feedback instance to provide position, velocity, and acceleration data used by Safety Stop Functions. | 0=No Feedback (default) 1=Primary Channel
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 21 | Safety Feedback Fault | Status | Get | BOOL | Provides a copy of Feedback Status from the Safety Feedback instance. | 0=No Fault 1=Faulted
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 22 | Safety Feedback Fault Type | Status | Get | USINT | Combined Feedback Fault Reasons for Safety Feedback Fault from both the Primary Safety Feedback instance (‘1’ suffix) and Secondary Safety Feedback instance (‘2’ suffix) associated with this Safety Stop Functions object. | 1=No Fault 2=Invalid configuration 3=Exceeded max speed 4=Exceeded max acceleration 5=Sin2+Cos2 error 6=Quadrature error 7=Discrepancy error 8=Partner faulted 9=Supply voltage error 10=Feedback Signal Noise 1 11=Feedback Signal Lost 1 See Safety Feedback Faults in the user manual for details.
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 30 | Safety Function Fault | Status | Get | BOOL | The logical OR of: • Safety Stop Fault (attribute 31) • Safety Limit Fault (attribute 32) • Safety Feedback Fault (attribute 21) | 0=No Fault 1=Faulted
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 31 | Safety Stop Fault | Status | Get | BOOL | The logical OR of: • STO Fault (attribute 263) • SS1 Fault attribute (283) • SBC Fault (attribute 363) | 0=No Fault 1=Faulted
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 32 | Safety Limit Fault | Status | Get | BOOL | Logical OR of all Limit Fault attributes that reference this instance. | 0=No Fault 1=Faulted
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 33 | Safety Limit Active | Status | Get | BOOL | Logical OR of all Limit Active attributes that reference this instance. | 0=No Limit 1=Limit is Active
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 34 | Restart Required | Status | Get | BOOL | Indicates if stop function has been activated when the Restart Type is Manual. | 0=Restart Not Required 1=Restart Required
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 40 | Safety Stop Status | Status | Get | WORD | Indicates the value of a collection of Safety Stop Status bits. See Values. | Bits ¦Value (0=False, 1=True) 0: Safety Function Fault 1: Safety Reset 2: Restart Required 3: STO Active 4: Torque Disabled 5: SBC Active (S4, S5) 6: Brake Engaged (S4, S5) 7: SS1 Active (S4, S5)
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 41 | Safety Stop Faults | Status | Get | WORD | Collection of Safety Stop Fault bits. See Values. | Bits ¦Value (0=False, 1=True) 2: Feedback Fault 3: STO Fault 4: SS1 Fault 7: SBC Fault
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 50 | Connection Loss Action | Configuration | Set (1) | USINT | Defines the action to take if the Safety Output connection is lost (or closed). | 0=STO 1=SS1
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 51 | Connection Idle Action | Configuration | Set (1) | USINT | Defines the action to take if the Safety Output connection transitions from Run to Idle. | 0=STO 1=SS1
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 100 | Safety IO Status | Status | Get | WORD | State of MPU inputs | Bits ¦Value (0=False, 1=True) 0: PWM Power 1: PWM Enable A 2: Enable Status A 3: Safe Input A 8: Pulse Test Enable 9: PWM Enable B 10: Enable Status B 11: Power Status 12: Safe Input B
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 101 | STO Delay | Configuration | Set (1) | UINT | Specify delay time from STO Active to Torque Disabled. This delay allows the time for an external brake to engage before torque disabled. | 0…65335 ms Default=0
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 110 | SBC Ready | Status | Get | BOOL | Indicates whether the Safe Brake Control safety function is supported, configured, and ready for operation. | 0=Not Ready 1=Ready
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 111 | SS1 Ready | Status | Get | BOOL | Indicates whether the Safe Stop 1 safety function is supported, configured, and ready for operation. | 0=Not Ready 1=Ready
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 115 | STO Ready | Status | Get | BOOL | Indicates whether the Safe Torque off is configured and ready for operation. | 0=Not Ready 1=Ready
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 260 | STO Mode | Status | Get | USINT | Indicates the current Safe torque off mode. | 0=Reserved 1=Used (default) 2=Permit Torque
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 261 | STO Output | Configuration | Set (1) | BOOL | Enables or disables energy to the motor which can generate torque (or force in the case of a linear motor). This is safety data. | 0=Disable Torque 1=Permit Torque The safe state of this safety data is 0.
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 262 | STO Active | Status | Get | BOOL | Indicates the output of STO Activation block. | 0=Permit Torque 1=Disable Torque
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 263 | STO Fault | Status | Get | BOOL | Indicates when a Safe Torque Off fault occurs. | 0=No Fault 1=Faulted
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 264 | STO Fault Type | Status | Get | USINT | Provides detailed information about an STO fault. | 1=No Fault 3=Circuit Error 102=Hardwired Input Discrepancy 104=Hardwired Input Active in Network Mode 105=Both Pairs Active
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 265 | STO Activation | Status | Get | BYTE | Indicates the status of all inputs to the STO Activation block. | Bits ¦Value (0=False, 1=True) 0: STO Output Active - Set when STO Output = Disable Torque. Cleared by a restart. 1: SS1 Complete - Set at the SS1 Max Stop Time or when device is at SS1 Standstill Speed. Cleared by a safety reset. 2: Safety Stop Fault - Set by any Safety Stop Functions fault. Cleared by a safety reset. 3: Safety Limit Fault - Set by any Safety Limit Functions fault. Cleared by a safety reset. 4: Safety Limit Active - Set by a Safety Limit Function with Limit Action = STO. Cleared by a safety reset. 5: Connection Loss 6: Connection Idle
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 266 | Torque Disabled | Status | Get | BOOL | Indicates the status of safe torque off. | 0=Torque Disabled 1=Torque Permitted
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 280 | SS1 Mode | Status | Set | USINT | Defines Safe Stop 1 mode. | 0=Not Used 1=Timed SS1 2=Monitored SS1
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 281 | SS1 Request | Status | Set | BOOL | Selects a Safe Stop 1 request. | 0=No Request 1=Request
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 282 | SS1 Active | Status | Get | BOOL | Indicates whether the Safe Stop 1 function is active. | 0=Not Active 1=Active
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 283 | SS1 Fault | Status | Get | BOOL | Indicates when a Safe Stop 1 fault has occured. | 0=No Fault 1=Faulted
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 284 | SS1 Fault Type | Status | Get | USINT | Describes detailed information about the Fault. | 1=No Fault 2=Invalid Configuration 3=Deceleration Rate 4=Maximum Time 5=Feedback Invalid
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 286 | SS1 Standstill Speed | Configuration | Set (1) | REAL | Defines the speed below which motion is considered stopped. | Default=0.0 Feedback Units/s
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 287 | SS1 Stop Monitor Delay | Configuration | Set (1) | UINT | Defines the delay before deceleration is monitored. | 0…65535 ms Default=0 ms
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 288 | SS1 Decel Ref Rate | Configuration | Set (1) | REAL | Defines the minimum rate of deceleration while stopping. | Feedback Units / s² Default=0.0 Feedback Units/s2 , which means no deceleration monitoring
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 289 | SS1 Activation | Status | Get | BYTE | Indicates the source of the SS1 activation. | Bits ¦Value (0=False, 1=True) 0: SS1 Request 1: Safe Limit Active 2: Connection Loss 3: Connection Idle
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 290 | SS1 Decel Ref Tolerance | Configuration | Set (1) | REAL | Defines the speed tolerance applied to the deceleration ramp check. | Default=0.0 Feedback Units/s
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 291 | SS1 Ext Max Stop Time | Configuration | Set (1) | UDINT | Defines the allowed time to stop. | 0…4294967296 ms Default = 0 ms
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 360 | SBC Mode | Configuration | Set (1) | USINT | Defines the Safe Brake Control function mode. | 0=Not Used 1=Used No Pulse Test 2=Used Pulse Test
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 361 | SBC Output | Configuration | Set (1) | BOOL | Status of SBC Activations. This is safety data. | 0=Engage Brake 1=Release Brake Permit The safe state of this safety data is 0.
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 362 | SBC Active | Status | Get | BOOL | Indicates the output of SBC Activation block. | 0=Release Brake 1=Engage Brake
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 363 | SBC Fault | Status | Get | BOOL | Indicates when a Safe brake control fault has occured. | 0=No Fault 1=Faulted
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 364 | SBC Fault Type | Status | Get | USINT | Describes detailed information about the Fault. | 1=No fault 2=Invalid Configuration
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 365 | SBC Activation | Status | Get | BYTE | Indicates the status of all brake inputs to the SBC Activation block. | Bits ¦Value (0=False, 1=True) 0=SBC Output Active 1=STO Active 2=Fault
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 366 | Brake Engaged | Status | Get | BOOL | Indicates the status of Safe Brake Control. | 0=Brake Released 1=Brake Engaged
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 367 | SBC Output Monitor Value | Status | Get | BOOL | Monitors safe brake output; that is, the output value at the terminal screw. | 0=Brake Deenergized 1=Brake Energized
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 368 | STO Activates SBC | Configuration | Set (1) | USINT | Specifies whether torque off and brake release are linked. | 0=Not Linked (default) 1=Linked
0x005A (90) | Safety Stop Functions Object | 1= Single Axis | 369 | STO to SBC Delay | Configuration | Set (1) | INT | Defines the delay between STO activation and SBC activation. For negative values, brake engage is immediate and torque disable is delayed. | -32768 … 32767 ms Default=0 ms
0x0348 (840) | Safety Dual Channel Input | 1 = first input pair 2 = second input pair | 3 | Dual Channel Mode | Configuration | Set (1) | USINT | Selects the mode for the two channels of the Safety Dual Channel Input. | 0=Single Channel 1=Dual Channel Equivalent 2=Dual Channel Complementary
0x0348 (840) | Safety Dual Channel Input | 1 = first input pair 2 = second input pair | 4 | Dual Channel Evaluation Status | Status | Get | BOOL | Indicates the status of the dual channel evaluation. | 0=Alarm 1=OK
0x0348 (840) | Safety Dual Channel Input | 1 = first input pair 2 = second input pair | 5 | Discrepancy Time Monitoring | Configuration | Set (1) | UINT | Defines the time limit at which the input discrepancy becomes an error. | 0…65565 ms Default=0 ms
-1 | Configuration attributes are settable only through the user interface of the configuration software.

## Standard IO Objects
Armor PowerFlex CIP Object Definitions
For more information see:
Armor PowerFlex AC Drives User Manual, publication 35-UM001.
Class | Name | Instance | Attribute | Attribute Name | Data Classification | Access Rule | Data Type | Description | Attribute Values
0x0008 (8) | Discrete Input Point | 1=IN0 2=IN1 3=IN2 4=IN3 5=IN/OUT0 6=IN/OUT1 7=KeypadF0 8=KeypadF1 9=KeypadF2 10=KeypadClear | 3 | Value | Status | Get | BOOL | Displays the input point value. | 0=Off 1=On
0x0008 (8) | Discrete Input Point | 1=IN0 2=IN1 3=IN2 4=IN3 5=IN/OUT0 6=IN/OUT1 7=KeypadF0 8=KeypadF1 9=KeypadF2 10=KeypadClear | 4 | Status | Status | Get | BOOL | Displays the input point status. | 0=OK 1=Alarm
0x0008 (8) | Discrete Input Point | 1=IN0 2=IN1 3=IN2 4=IN3 5=IN/OUT0 6=IN/OUT1 | 119 | Off On Delay | Configuration | Set(1) | UINT | Sets the filter time for an off to on transition. | 0…65535 ms Default=5 ms for standard I/O connection; default=0 ms for all other operating modes
|  | 7=KeypadF0 8=KeypadF1 9=KeypadF2 10=KeypadClear | 119 | Off On Delay | Constant | Get | UINT | Indicates the filter time for off to on transition. Value is always 10 ms for instances 7…10. | 10 ms
0x0008 (8) | Discrete Input Point | 1=IN0 2=IN1 3=IN2 4=IN3 5=IN/OUT0 6=IN/OUT1 | 120 | On Off Delay | Configuration | Set(1) | UINT | Filter time for on to off transition | 0…65535 ms Default=5 ms
|  | 7=KeypadF0 8=KeypadF1 9=KeypadF2 10=KeypadClear | 120 | On Off Delay | Constant | Get | UINT | Filter time for on to off transition | 100 ms
0x0008 (8) | Discrete Input Point | 1=IN0 2=IN1 3=IN2 4=IN3 5=IN/OUT0 6=IN/OUT1 7=KeypadF0 8=KeypadF1 9=KeypadF2 10=KeypadClear | 121 | Input Port Value | Status | Get | BOOL | Indicates the input point value at the terminal prior to the on/off delay evaluation. | 0=Off 1=On
0x0008 (8) | Discrete Input Point | 1=IN0 2=IN1 3=IN2 4=IN3 5=IN/OUT0 6=IN/OUT1 7=KeypadF0 8=KeypadF1 9=KeypadF2 10=KeypadClear | 123 | Sensor Power Fault | Status | Get | BOOL | Indicates whether a fault condition (such as overcurrent) exists for the sensor power being provided for the input. | 0=OK 1=Fault
0x0009 (9) | Discrete Output Point | 1=IN/OUT0 2=IN/OUT1 | 3 | Value | Status | Get | BOOL | Indicates the output point value. | 0=off 1=on
0x0009 (9) | Discrete Output Point | 1=IN/OUT0 2=IN/OUT1 | 4 | Status | Status | Get | BOOL | Indicates the output point status. | 0=OK 1=alarm
0x0009 (9) | Discrete Output Point | 1=IN/OUT0 2=IN/OUT1 | 12 | Object State | Status | Get | USINT | Displays the state of the object. | 1=Non-Existent 2=Available 3=Idle 4=Ready 5=Run 6=Recoverable Fault 7=Unrecoverable Fault 255=Reserved
0x0009 (9) | Discrete Output Point | 3= Test Output 0(2) 4= Test Output 1(2) | 13 | Test Output Mode for Safety | Configuration | Set | USINT | Configures the output point. | 0 = Not Used 2 = Test Output
0x0009 (9) | Discrete Output Point | 1=IN/OUT0 2=IN/OUT1 | 112 | Short Overload Fault | Status | Get | BOOL | Indicates whether a short circuit or overload fault condition is detected. | 0=OK 1=Fault
0x0009 (9) | Discrete Output Point | 1=IN/OUT0 2=IN/OUT1 | 129 | Active Source | Status | Get | UINT | Indicates the instance number of the Discrete Output Control Source (0x043F) instance currently actively controlling the output value (Value attribute 3). | See the Discrete Output Control Source (0x043F) instance Value attribute (3).
0x0009 (9) | Discrete Output Point | 3= Test Output 0(2) 4= Test Output 1(2) | 130 | Output Ready | Status | Get | BOOL | Indicates whether the output is ready. | 0=Not ready 1=Ready
-1 | Configuration attributes are settable only through the user interface of the configuration software.
-2 | Test outputs are only available on the bulletin 35S Armor PowerFlex drives.